## Main Abstract
MAIN ABSTRACT
S.No. | Operation Zone | No. of Substations with 33/11kV, 33/22kV, 66/11kV, 66/22kV, 132/11kV levels | Transformation Capacity Available (in MVA) | Surplus Transformation capacity which can be fed from RE Power Plants (in MW)
1 | Hamirpur | 62 | 551.1 | 127.7884
2 | Kangra | 79 | 625.5 | 216.3617
3 | Mandi | 56 | 393.45 | 170.5082
4 | Shimla | 82 | 1448.62 | 736.421
| Total | 279 | 3018.67 | 1251.0793

## Shimla Zone
Notification of sub-station & feeder wise surplus capacity which can be fed from RE Power Plants under Shimla Zone, Shimla.
Sr. No. | Name of Sub-Station | Transformation capacity Installed at 33/11 kV Level (MVA) | Minimum Surplus Transformation capacity available at 132/11kV, 33/11 kV & 33/22 kV Level (MW) |  |  |  | Remarks | Remarks ++
|  |  |  | Name of Feeder | Type of Conductor | Min Rational Capacity of Feeder as per Surplus Transformation Capacity (Without Minimum Loading of Feeder) (in MW)
1 | 33/11 kV Sub-Station. Kunihar | 12.6 | 6.1 | 11KV Domehar | ACSR 6/1/2.59, 6/1/3.35 mm (Mixed) | 0.5 | Verma SPP 250kW, DNS SPP 250 kW and BKT SPP 500kW
|  |  |  | 11KV Arki | ACSR 6/1/4.72mm | 1.375
|  |  |  | 11KV MES | ACSR 6/1/2.59, 6/1/3.35 mm (Mixed) | 1.375
|  |  |  | 11KV Deoli | ACSR 6/1/2.59mm | 0.875 | Parmesh SPP 500kW
|  |  |  | 11KV Kunihar local | ACSR 6/1/2.59, 6/1/2.11mm (Mixed) | 0.6 | Mamligh SPP 500kW
|  |  |  | 11KV Mamligh | ACSR 6/1/2.59, 6/1/3.35 mm (Mixed) | 1.375
2 | 33/11 kV Sub-Station. Arki | 6.3 | 3.3 | 11KV Arki Local Feeder | AAAC 7/4.26 | 0.55
|  |  |  | 11 KV Shalaghat Feeder | ACSR 6/1/2.59, AAAC 7/4.26 | 0.55
|  |  |  | 11 KV Galog Feeder | ACSR 6/1/2.59, AAAC 7/4.26 | 0.55
|  |  |  | 11 KV Batal Feeder | ACSR 6/1/2.59, AAAC 7/4.26 | 0.55 | Paavan E SPP 700kW
|  |  |  | 11 KV NCPC Feeder | AAAC 7/3.81 | 0.55
|  |  |  | 11 KV Shiv Ghatti Feeder | AAAC 7/3.81 | 0.55
3 | 33/11 kV Subathu | 6.3 | 4 | 11 KV Nauti Gaon | ACSR 6/1/3.35mm² | 0.666
|  |  |  | 11 KV Subathu | ACSR 6/1/3.35mm² | 0.666
|  |  |  | 11 KV MES Gamber | ACSR 6/1/3.35mm² | 0.666
|  |  |  | 11 KV Kuthar | ACSR 6/1/3.35mm² | 0.666
|  |  |  | 11 KV Solan | ACSR 6/1/3.35mm² | 0.666
|  |  |  | 11 KV Banalgi | ACSR 6/1/3.35mm² | 0.666
4 | 33/11 kV Garkhal | 12.6 | 6.4 | 11 Kv Kasauli | ACSR 6/1/4.72, ACSR 6/1/3.35, ACSR 6/1/2.59 | 0.64
|  |  |  | 11 Kv Old CRI | AAA 7/4.26, ACSR 6/1/3.35 | 0.64
|  |  |  | 11 Kv New CRI +MES | ACSR 6/1/4.72 | 0.64
|  |  |  | 11 Kv Jabli | ACSR 6/1/4.72 | 0.64
|  |  |  | 11 Kv Radar | ACSR 6/1/4.72 | 0.64
|  |  |  | 11 Kv Water Supply | ACSR 6/1/4.72, ACSR 6/1/3.35, ACSR 6/1/2.59 | 0.64
|  |  |  | 11 Kv Kotbeja | ACSR 6/1/4.72, ACSR 6/1/3.35, ACSR 6/1/2.59 | 0.64
|  |  |  | 11 Kv Tiron | ACSR 6/1/4.72 | 0.64
|  |  |  | 11 Kv Dharmpur No 1 | ACSR 6/1/4.72, ACSR 6/1/3.35, ACSR 6/1/2.59 | 0.64
|  |  |  | 11 Kv Dharmpur No 2 | ACSR 6/1/4.72, ACSR 6/1/3.35, ACSR 6/1/2.59 | 0.64
5 | 33/11 kV Gandhigram | 9.45 | 5.6 | 11KV Dharampur-V | ACSR 6/1/3.35MM | 0.7
|  |  |  | 11KV Dharampur-IV | ACSR 6/1/3.35MM | 0.7
|  |  |  | 11KV Gandhigram | ACSR 6/1/3.35MM | 0.7
|  |  |  | 11KV Kumarhatti | ACSR 6/1/3.35MM | 0.7
|  |  |  | 11KV Dagshai | ACSR 6/1/3.35MM | 0.7
|  |  |  | 11KV Sultanpur | ACSR 6/1/3.35MM | 0.7
|  |  |  | 11KV Bhojnagar | ACSR 6/1/3.35MM | 0.7
|  |  |  | 11KV Tata | ACSR 6/1/3.35MM | 0.7
6 | 33/11 kV Oachghat | 6.3 | 4 | 11 KV UHF Nauni | AAAC 7/3.81 mm² | 1
|  |  |  | 11 KV Maryog | AAAC 7/4.26 mm², | 1
|  |  |  | 11 KV Shamti | AAAC 7/3.81 mm² | 1
|  |  |  | 11 KV Jatoli | AAAC 7/4.26 mm², | 1
7 | 33/11 kV Basal | 12.6 | 7.5 | 11 KV Rabon | ACSR 6/1/4.72 mm² | 1.25
|  |  |  | 11 KV Gurudwara | AB Cable 185mm², ACSR 6/1/4.72 mm² | 1.25
|  |  |  | 11 KV Lavighat | AB Cable 185mm², ACSR 6/1/4.72 mm² | 1.25
|  |  |  | 11 KV Circle | AB Cable 185mm² | 1.25
|  |  |  | 11KV Barog | ACSR 6/1/4.72 mm² | 1.25 | GM SPP 250kW
|  |  |  | 11 KV Deonghat | ACSR 6/1/4.72 mm² | 1.25
8 | 33/11 kV Kather | 30 | 13 | 11 KV Sarahan | ACSR 6/1/2.59, 30mm², AB Cable 120mm² | 1
|  |  |  | 11 KV Chambaghat | AAAC 7/3.15 mm², ACSR 6/1/4.72 mm² | 1
|  |  |  | 11 KV WSS | ACSR 6/1/4.72 mm² & 6/1/2.11mm², AAAC 7/3.15 | 1
|  |  |  | 11 KV Himachal Conductor | ACSR 6/1/4.72 mm² | 1
|  |  |  | 11 KV Rajgarh | ACSR 6/1/2.59, 30mm², AB Cable 185mm² | 1
|  |  |  | 11 KV Lavighat | AB Cable 185mm², ACSR 6/1/4.72 mm² | 1
|  |  |  | 11 KV Solan No-I | ACSR 6/1/4.72 mm², ABC 185 mm | 1
|  |  |  | 11 KV Solan No-II | AAAC 7/4.26, 100 mm² & AB Cable 240 mm², 185 & 120 mm² | 1
|  |  |  | 11 KV Solan No-III | ACSR 6/1/4.72 mm², XLPE 185 mm | 1
|  |  |  | 11 KV Solan No-IV | AAAC 7/3.81,80mm² & AB Cable 185 mm² & 120 mm² | 1
|  |  |  | 11 KV Kandaghat | ACSR 6/1/4.72 mm² & 6/1/2.11mm² | 1
|  |  |  | 11 KV MES | AB Cable 185mm²/120 mm² | 1
|  |  |  | 11 KV Shivalik | AAAC 7/3.15 mm², | 1
9 | 33/11 kV Substation Kandaghat | 12.6 | 7.5 | 11 KV Kandaghat | ACSR 6/1/3.35 mm² | 1.25
|  |  |  | 11 KV Chail | ACSR 6/1/3.35mm², 6/1/2.11, 7/3.15,7/4.26 | 1.25
|  |  |  | 11 KV Dochi | ACSR 6/1/3.35mm², 6/1/2.11, 7/3.15 | 1.25
|  |  |  | 11 KV Chhausha | AAAC 7/3.81 mm² | 1.25
|  |  |  | 11 KV Vaknaghat | AAAC 7/3.81 mm² | 1.25
|  |  |  | 11 KV Kather (old kandaghat) | AAAC 7/3.81 mm² | 1.25
10 | 33/11 kV Sarahan | 6.3 | 3.3 | 11 KV Thakurdwara | AAAC 7/3.15MM2 | 0.55 | Bhureshwar Mahadev SPP 500kW
|  |  |  | 11 KV Srahan-Local | AAAC 7/3.15MM2 | 0.55
|  |  |  | 11 KV Banah ki Ser | AAAC 7/3.15MM2 | 0.55
|  |  |  | 11 KV Dhangyar Feeder | ACSR 6/1/2.59MM2 | 0.55
|  |  |  | 11 KV Tikkari Pajeli | ACSR 6/1/2.59MM2 | 0.55 | Naina Tikker SPP 250 kW
|  |  |  | 11 KV Srn-Narag | AAAC 7/3.15MM2 | 0.55
11 | 33/11 kV Bagthan | 3.15 | 2.268 | 11 KV Banethi | ACSR 6/1/2.59mm. Sq | 0.567
|  |  |  | 11 KV Parara | ACSR 6/1/2.59mm. Sq | 0.567
|  |  |  | 11 KV Gee Matlana | ACSR 6/1/2.59mm. Sq | 0.567
|  |  |  | 11 KV Dinger Kinner | ACSR 6/1/2.59mm. Sq | 0.567
12 | 33/11 kV Ramshehar Sub-Station | 3.15 | 0 | 11 KV Kumar Hatti | ACSR 6/1/3.35 & AAAC 7/3.81 | 0 |  | KK Kashyap 2 MW and Nand Solar 5 MW at 33kV level
|  |  |  | 11 KV Sunna | ACSR 6/1/2.59 & 6/1/2.11 | 0 | Kasla SPP 500kW & Swarghat SPP 350kW
|  |  |  | 11 KV Chamdar | ACSR 6/1/2.11 & 6/1/2.59 | 0 | Apex Solar, Aditya Urja Solar & Dhiman Electrical Solar 500kW each
|  |  |  | 11 KV Diggal | ACSR 6/1/3.35 & 6/1/2.59 | 0
13 | 33/11 kV Manjholi | 20 | 12.96 | 11 KV Khurana | ACSR 6/1/3.35 | 2.1536
|  |  |  | 11 KV Dherowal-I | ACSR 6/1/4.72 & 6/1/3.35 | 2.1536
|  |  |  | 11 KV Dherowal-II | ACSR 6/1/4.72 | 2.192 | Jai Gurasees and Rudra Transport Co. 600 kW each
|  |  |  | 11 KV S.R.Mills | ACSR 6/1/3.35 | 2.1536
|  |  |  | 11 KV Aradhana | ACSR 6/1/3.35 | 2.1536 | Shiv Shakti Solar Farm & Balaji SPP 1 MW each
|  |  |  | 11 KV Manjholi | ACSR 6/1/3.35 | 2.1536
14 | 66/33/11 kV Sub-Station Baglehar | 20 | 10.554 | 11 KV Joghon | ACSR 6/1/3.35 | 0.5 | Chamba SPP 500kW, Aditya Urja-II 1 MW & SKS Green Energy 600kW
|  |  |  | 11 KV Baroona | ACSR 6/1/3.35 | 1.5 | Himachal Green SPP 750 kW
|  |  |  | 11 KV Bhogpur | ACSR 6/1/4.72 | 2
|  |  |  | 11 KV Kotla | ACSR 6/1/3.35 | 1.4 | RDVP SPP 765kW
|  |  |  | 11 KV Saror | ACSR 6/1/2.11 | 2
|  |  |  | 11kV Adhuwal | ACSR 6/1/2.11 | 1 | RDVP-II SPP 500kW
|  |  |  | 11 KV Kashmirpur | ACSR 6/1/3.35 | 2.1536
15 | 66/11 kV Sub-Station Nalagarh | 40 | 28.8 | 11 KV Aside Feeder | AAAC 7/4.26 | 1.9454
|  |  |  | 11 KV Barotiwala Feeder | AAAC 7/3.81 | 1.9454
|  |  |  | 11 KV G. Claridge Feeder | AAAC 7/4.26 | 1.9454
|  |  |  | 11 KV Industrial Feeder | ACSR 6/1/3.35 | 1.9454
|  |  |  | 11 KV Him Chem Feeder | ACSR 6/1/3.35 | 1.9454
|  |  |  | 11 KV Panjehra Feeder | AAAC 7/4.26 | 1.9454
|  |  |  | 11 KV Dabhota Feeder | AAAC 7/3.15 | 1.9454
|  |  |  | 11 KV Pooja Cotspin | AAAC 7/4.26 | 1.9454
|  |  |  | 11 KV Ramshehar Feeder | ACSR 6/1/3.35 & 6/1/2.59 | 1.5638 | Amar Green Solar Farm 600kW
|  |  |  | 11 KV Nalagarh Feeder | AAAC 7/4.26 | 1.9454
|  |  |  | 11 KV MIDC Feeder | AAAC 7/4.26 | 1.9454
|  |  |  | 11 KV Godrej Feeder | AAAC 7/4.26 | 1.9454
|  |  |  | 11 KV Khera No.-I Feeder | AAAC 7/3.81 | 1.9454
|  |  |  | 11 KV Dattowal Feeder | AAAC 7/3.81 | 1.9454
|  |  |  | 11 KV Khera No.-II Feeder | AAAC/7/4.26 | 1.9454
16 | 66/11 kV Sub-Station Sanehar | 20 | 14.4 | 11 KV Panjehra-2 Feeder | ACSR 6/1/4.72 | 3.2785
|  |  |  | 11 KV Industrial-2 Feeder | ACSR 6/1/4.72 | 3.2785
|  |  |  | 11KV Dhabota-2 Feeder | ACSR 6/1/4.72 | 3.2785
|  |  |  | 11KV Dattowal-2 Feeder | ACSR 6/1/4.72 | 3.2785
17 | 66/11 kV Sub-Station Akanwali | 20 | 14.4 | 33 KV FEEDER NO 1 | ACSR 6/1/4.72 100sqmm | 0.75789
|  |  |  | 33 KV FEEDER NO 2 | ACSR 6/1/4.72 100sqmm | 0.75789
|  |  |  | 33 KV FEEDER NO 3 | ACSR 6/1/4.72 100sqmm | 0.75789
|  |  |  | 33 KV FEEDER NO 4 | ACSR 6/1/4.72 100sqmm | 0.75789
|  |  |  | 33 KV FEEDER NO 5 | ACSR 6/1/4.72 100sqmm | 0.75789
|  |  |  | 11 KV FEEDER NO 1 | AAAC 7/4.26 | 0.75789
|  |  |  | 11 KV FEEDER NO 4 | AAAC 7/4.26 | 0.75789
|  |  |  | 11 KV FEEDER NO 5 | AAAC 7/4.26 | 0.75789
|  |  |  | 11 KV FEEDER NO 6 | AAAC 7/4.26 | 0.75789
|  |  |  | 11 KV FEEDER NO 8 | AAAC 7/4.26 | 0.75789
|  |  |  | 11 KV FEEDER NO 9 | AAAC 7/4.26 | 0.75789
|  |  |  | 11 KV FEEDER NO 10 | AAAC 7/4.26 | 0.75789
|  |  |  | 11 KV FEEDER NO 11 | AAAC 7/4.26 | 0.75789
|  |  |  | 11 KV FEEDER NO 12 | AAAC 7/4.26 | 0.75789
|  |  |  | 11 KV FEEDER NO 13 | AAAC 7/4.26 | 0.75789
|  |  |  | 11 KV FEEDER NO 15 | AAAC 7/4.26 | 0.75789
|  |  |  | 11 KV FEEDER NO 16 | AAAC 7/4.26 | 0.75789
|  |  |  | 11 KV FEEDER NO 17 | AAAC 7/4.26 | 0.75789
|  |  |  | 11 KV FEEDER NO 18 | AAAC 7/4.26 | 0.75789
18 | 66/11 kV Sub-Station Davni | 40 | 28.8 | 11 KV FEEDER NO 1 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 2 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 3 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 4 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 9 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 10 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 11 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 12 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 13 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 14 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 15 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 16 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 17 | AAAC 7/4.26 | 2.2154
19 | 66/11 kV Sub-Station Batoli Kalan | 40 | 28.8 | 11 KV FEEDER NO 1 | ACSR 6/1/4.72 100sqmm | 2.2154
|  |  |  | 11 KV FEEDER NO 2 | ACSR 6/1/4.72 100sqmm | 2.2154
|  |  |  | 11 KV FEEDER NO 3 | ACSR 6/1/4.72 100sqmm | 2.2154
|  |  |  | 11 KV FEEDER NO 5 | ACSR 6/1/4.72 100sqmm | 2.2154
|  |  |  | 11 KV FEEDER NO 6 | ACSR 6/1/4.72 100sqmm | 2.2154
|  |  |  | 11 KV FEEDER NO 7 | ACSR 6/1/4.72 100sqmm | 2.2154
|  |  |  | 11 KV FEEDER NO 8 | ACSR 6/1/4.72 100sqmm | 2.2154
|  |  |  | 11 KV FEEDER NO 9 | ACSR 6/1/4.72 100sqmm | 2.2154
|  |  |  | 11 KV FEEDER NO 10 | ACSR 6/1/4.72 100sqmm | 2.2154
|  |  |  | 11 KV FEEDER NO 11 | ACSR 6/1/4.72 100sqmm | 2.2154
|  |  |  | 11 KV FEEDER NO 12 | ACSR 6/1/4.72 100sqmm | 2.2154
|  |  |  | 11 KV FEEDER NO 13 | ACSR 6/1/4.72 100sqmm | 2.2154
|  |  |  | 11 KV FEEDER NO 14 | ACSR 6/1/4.72 100sqmm | 2.2154
20 | 66/11 kV Sub-Station Malpur | 40 | 28.8 | 33KV Feeder no 1 | ACSR 30/7/2.59 100sqmm | 3.3173
|  |  |  | 33 KV Feeder no 2 | ACSR 30/7/2.59 100sqmm | 3.3173
|  |  |  | 33 Kv Feeder no 3(Cipla) | ACSR 30/7/2.59 100sqmm | 3.3173
|  |  |  | 11 KV FEEDER NO 1 | AAAC 7/4.26 | 3.1413
|  |  |  | 11 KV FEEDER NO 2 | AAAC 7/4.26 | 3.1413
|  |  |  | 11 KV FEEDER NO 3 | AAAC 7/4.26 | 3.1413
|  |  |  | 11 KV FEEDER NO 4 | AAAC 7/4.26 | 3.1413
|  |  |  | 11 KV FEEDER NO 5 | AAAC 7/4.26 | 3.1413
|  |  |  | 11 KV FEEDER NO 7 | AAAC 7/4.26 | 3.1413
21 | 132/11 kV Sub-Station Barotiwala | 63 | 44.36 | 11 KV USV | AAAC 7/4.26 | 1.7744
|  |  |  | 11 KV BADDI-1 | AAAC 7/4.26 | 1.7744
|  |  |  | 11 KV UT | AAAC 7/4.26 | 1.7744
|  |  |  | 11 KV EPIP-1 | AAAC 7/4.26 | 1.7744
|  |  |  | 11 KV SR FORGING | AAAC 7/4.26 | 1.7744
|  |  |  | 11 KV EPIP-4 | AAAC 7/4.26 | 1.7744
|  |  |  | 11 KV HILL TOP | AAAC 7/4.26 | 1.7744
|  |  |  | 11 KV Haripur | AAAC 7/4.26 | 1.7744
|  |  |  | 11 KV OPTECH | AAAC 7/4.26 | 1.7744
|  |  |  | 11 KV BADDI-2 | AAAC 7/4.26 | 1.7744
|  |  |  | 11 KV EPIP-3 | AAAC 7/4.26 | 1.7744
|  |  |  | 11 KV BADDI-3 | AAAC 7/4.26 | 1.7744
|  |  |  | 11 KV EPIP-2 | AAAC 7/4.26 | 1.7744
|  |  |  | 11 KV PATTA | AAAC 7/4.26 | 1.7744
|  |  |  | 11 KV EPIP-5 | AAAC 7/4.26 | 1.7744
|  |  |  | 11 KV BAROTIWALA 6 | AAAC 7/4.26 | 1.7744
|  |  |  | 11 KV BAROTIWALA-2 | AAAC 7/4.26 | 1.7744
|  |  |  | 11 KV BAROTIWALA-3 | AAAC 7/4.26 | 1.7744
|  |  |  | 11 KV BAROTIWALA 5 | AAAC 7/4.26 | 1.7744
|  |  |  | 11 KV BAROTIWALA 4 | AAAC 7/4.26 | 1.7744
|  |  |  | 11 KV BARORIWALA 7 | AAAC 7/4.26 | 1.7744
|  |  |  | 11 KV BAROTIWALA 1 | AAAC 7/4.26 | 1.7744
|  |  |  | 11 KV BAROTIWALA 8 | AAAC 7/4.26 | 1.7744
|  |  |  | 11 KV Sarvottam care | AAAC 7/4.26 | 1.7744
|  |  |  | 11 KV BAROTIWALA 10 | AAAC 7/4.26 | 1.7744
22 | 66/11 kV Sub-Station Parwanoo | 40 | 23.04 | 11KV PARWANOO 1st | AAAC 7/4.26mm | 1.92
|  |  |  | 11KV PARWANOO 2nd | AAAC 7/4.26mm | 1.92
|  |  |  | 11KV PARWANOO 3rd | ACSR 6/1.4.72mm/AAAC 7/4.26mm | 1.92
|  |  |  | 11KV PARWANOO 4th | AAAC 7/4.26mm | 1.92
|  |  |  | 11KV PARWANOO 5th | ACSR 6/1.4.72mm/AAAC 7/4.26mm | 1.92
|  |  |  | 11KV PARWANOO 6th | AAAC 7/4.26mm | 1.92
|  |  |  | 11KV PARWANOO AB Tools | AAAC 7/4.26mm | 1.92
|  |  |  | 11KV PARWANOO Cosmo | ACSR 6/1.4.72mm/AAAC 7/4.26mm | 1.92
|  |  |  | 11KV PARWANOO Gabrial | ACSR 6/1.4.72mm/AAAC 7/4.26mm | 1.92
|  |  |  | 11KV PARWANOO Kasauli | ACSR 6/1.4.72mm/AAAC 7/4.26mm | 1.92
|  |  |  | 11KV PARWANOO Water Supply | ACSR 6/1.4.72mm/AAAC 7/4.26mm | 1.92
|  |  |  | 11KV PARWANOO Khadeen | ACSR 6/1.4.72mm/AAAC 7/4.26mm | 1.92
23 | 66/11 kV Sub-Station Mandhala | 80 | 46.08 | 11 KV Feeder No.6 | AAAC 7/4.26 | 3.1413
|  |  |  | 11 KV Feeder No.8 | AAAC 7/4.26 | 3.1413
|  |  |  | 11 KV Feeder No.9 | AAAC 7/4.26 | 3.1413
|  |  |  | 11 KV Feeder No.10 | AAAC 7/4.26 | 3.1413
|  |  |  | 11 KV Feeder No.11 | AAAC 7/4.26 | 3.1413
|  |  |  | 11 KV Feeder No.15 | AAAC 7/4.26 | 3.1413
|  |  |  | 11 KV Feeder No.16 | AAAC 7/4.26 | 3.1413
|  |  |  | 11 KV Feeder No.17 | AAAC 7/4.26 | 3.1413
|  |  |  | 11 KV Feeder No.18 | AAAC 7/4.26 | 3.1413
24 | 33/11 kV Goela Sub Station | 3.15 | 2 | 11KV Badhlag | 6/1/3.35 | 0.333
|  |  |  | 11KV Darwa | 6/1/3.35 | 0.333
|  |  |  | 11KV Goela | 6/1/3.35 | 0.333
|  |  |  | 11KV Bhaguri | 6/1/3.35 | 0.333
|  |  |  | 11KV Kandol | 6/1/3.35 | 0.333
|  |  |  | 11KV gharer | 6/1/3.35 | 0.333
25 | 66/11 kV Sub-Station Totu | 20 | 14 | 11 kV MES Feeder | 6/1/2.59 and 6/1/3.35 ACSR Conductor | 2
|  |  |  | 11 kV Banuti Feeder | 6/1/2.59 and 6/1/3.35 ACSR Conductor | 2
|  |  |  | 11 kV Chilling Plant Feeder | 6/1/2.59 and 6/1/3.35 ACSR Conductor | 2
|  |  |  | 11 kV Gadog Feeder | 6/1/2.59 and 6/1/3.35 ACSR Conductor | 2
|  |  |  | 11 kV Totu-Taradevi Feeder | 6/1/4.72 ACSR Conductor | 2
|  |  |  | 11 kV Chakker | ACSR Cond. 6/1/4.72 | 2
|  |  |  | 11 kV Summerhill | ACSR Cond. 6/1/4.72 | 2
26 | 33/11 kV Sub-Station Summerhill | 12.6 | 6 | 11 KV Boys Hostel Feeder | XLPE 300 mm2 | 1
|  |  |  | 11 KV Keneddy House Feeder | XLPE 300 mm2 | 1
|  |  |  | 11 KV Teacher House Feeder | XLPE 300 mm2 | 1
|  |  |  | 11 KV Kumar House Feeder | XLPE 300 mm2 | 1
|  |  |  | 11 KV AIR Feeder | XLPE 300 mm2 | 1
|  |  |  | 11 kV Old Supply (Doordarshan) | XLPE 300 mm2 | 1
27 | 33/11 kV Sub-Station Idgah | 20 | 9 | 11 KV DDU Ripon | 300/400 mm2 (300A) | 1.8
|  |  |  | 11 kV Co.Op. Bank Ridge | 300/400 mm2 (300A) | 1.8
|  |  |  | 11 kV North View | 300/400 mm2 | 1.8
|  |  |  | 11 kV Mythe | 300/400 mm2 | 1.8 | Idle Feeder
|  |  |  | 11 kV New Grand Hotel | 300/400 mm2 | 1.8 | Idle Feeder
28 | 33/11 kV Sub-Station Khallini | 20 | 14.4 | 11 KV Benmore Feeder | 6/1/4.72 & XLPE Cable 300 mm2 (240&576A) | 1.6
|  |  |  | 11 KV Kanlog Feeder | 6/1/4.72 & XLPE Cable 400 mm2 (240&650A) | 1.6
|  |  |  | 11 KV Bamloe Feeder | 6/1/4.72 & XLPE cable 300mm2 (240 & 576A) | 1.6
|  |  |  | 11 KV Forest Feeder | 6/1/4.72 & XLPE cable 300 mm2 (240& 576A) | 1.6
|  |  |  | 11 KV New Shimla Feeder | AAAC 7/4.26, AAAC 7/3.15 | 1.6
|  |  |  | 11 KV Palika Bhawan Feeder | 6/1/4.72 & XLPE cable 240 mm2 (240 & 513A) | 1.6
|  |  |  | 11 KV Alu Park Feeder | 6/1/4.72 & XLPE Cable 300mm2 (240 & 576A) | 1.6
|  |  |  | 11 KV Baragaon Feeder | AAAC 7/4.26, AAAC 7/3.15 | 1.6
|  |  |  | 11 KV Lower Khallini Feeder | 6/1/4.72 | 1.6
29 | 33/11 kV Sub-Station Bharari | 20 | 14 | 11 KV Bharari Feeder | 30/7/2.59 | 1.4
|  |  |  | 11 KV Belvedere Feeder | 6/1/4.72 | 1.4
|  |  |  | 11 KV Idgah Feeder | 6/1/4.72 | 1.4
|  |  |  | 11 KV D/Poabo Feeder | xlpe3*150mm2, 6/1/4.72 | 1.4
|  |  |  | 11 KV Telegraph Feeder | 6/1/4.72 & XLPE cable 400 mm2 | 1.4
|  |  |  | 11 KV Barmu Feeder | xlpe-3*95mm2,ACSR 6/1/3.35 | 1.4
|  |  |  | 11 KV Walker Feeder | 6/1.4.72 | 1.4
|  |  |  | 11 KV Ellysium Feeder | 6/1/4.72 | 1.4
|  |  |  | 11 KV Colony Feeder | XLPE cable 185mm2 | 1.4
|  |  |  | 11 KV Ragyan Feeder | xlpe-3*400mm2,ACSR 6/1/3.35 | 1.4
30 | 33/11 kV Sub-Station Shoghi | 6.3 | 4 | 11 KV Supermax Feeder | 6/1/2.59 and 6/1/3.35 ACSR Conductor | 1
|  |  |  | 11KV Tikasha Feeder | 6/1/2.59 and 6/1/3.35 ACSR Conductor | 1
|  |  |  | 11 KV Shoghi H/Board | 6/1/2.59 and 6/1/3.35 ACSR Conductor | 1
|  |  |  | 11 KVPaoghat K/ Chowki Feeder | 6/1/2.59 and 6/1/3.35 ACSR Conductor | 1
31 | 33/11 kV Sub-Station Taradevi | 12.6 | 8.4 | 11 KV Chamrog Feeder | 6/1/3.35 ACSR Conductor | 1.2
|  |  |  | 11 KV Kachi Ghatti Feeder | AAA 7/3.81, 6/1/2.59 ACSR Conductor | 1.2
|  |  |  | 11 KV Taradevi Feeder | 6/1/4.72 ACSR Cond. | 1.2
|  |  |  | 11 KV H.P.Press Feeder | 400 & 6/1/4.72 ACSR | 1.2
|  |  |  | 11 KV Barrier Feeder | 400 & 6/1/4.72 ACSR | 1.2
|  |  |  | 11 KV District Court Feeder | 3c*240 mm2, 6/1/4.72 ACSR Conductor | 1.2
|  |  |  | 11 KV Elephant Energy Feeder | 6/1/4.72 ACSR | 1.2
32 | 33/11 kV Sub-Station Ghandal | 3.15 | 2 | 11 KV Dhami Feeder | ACSR 6/1/3.35 & 6/1/2.59 | 0.333
|  |  |  | 11 KV Ghanahatti Feeder | ACSR 6/1/3.35 & 6/1/2.59 | 0.333
|  |  |  | 11 KV Shakrah Feeder | ACSR 6/1/3.35 & 6/1/2.59 | 0.333
|  |  |  | 11 KV Kohbagh Feeder | ACSR 6/1/3.35 & 6/1/2.59 | 0.333
|  |  |  | 11 KV Judicial Academy -I Feeder | ACR 6/1/4.72 mm2 | 0.333
|  |  |  | 11 KV Judicial Academy -2 Feeder | ACR 6/1/4.72 mm3 | 0.333
33 | 33/11 kV Sub-Station Sainj- Nallah | 6.3 | 4 | 11kV Sainj Nallah Stage Phase-1 | ACSR 6/1/2.59 MM | 1
|  |  |  | 11kV Sainj Nallah Stage Phase-2 | ACSR 6/1/2.59 MM | 1
|  |  |  | 11kV Sainj Nallah Stage Phase-3 | ACSR 6/1/3.35 MM | 1
|  |  |  | 11kV Sainj Nallah Stage Phase-4 | ACSR 6/1/3.35 MM | 1
34 | 33/11 kV Sub-Station Banuti | 6.3 | 4 | 11 kV Heera Nagar | 6/1/2.59 and 6/1/3.35 ACSR Conductor | 1
|  |  |  | 11 kV Dudhalti | 6/1/2.59 and 6/1/3.35 ACSR Conductor | 1
|  |  |  | 11 kV Rehal Bychari | 6/1/2.59 and 6/1/3.35 ACSR Conductor | 1
|  |  |  | 11 kV Local Banuti | 6/1/2.59 and 6/1/3.35 ACSR Conductor | 1
35 | 33/11 kV Sub-Station Maliana | 20 | 14 | 11 KV PC Kasumpti Feeder | 6/1/3.35 | 1.4
|  |  |  | 11 KV Strawberry Feeder | 6/1/4.72 & XLPE cable 240m2 (240& 513A) | 1.4
|  |  |  | 11 KV Kasumpti O/H Feeder | 6/1/4.72 | 1.4
|  |  |  | 11 KV Nav Bahar Feeder | 6/1/4.72 ACSR | 1.4
|  |  |  | 11 KV Cemetery Feeder | 6/1/3.35 | 1.4
|  |  |  | 11 KV New Flower Dale Feeder | 6/1.4.72 & XLPE cable 300 mm2 (240&576A) | 1.4
|  |  |  | 11 KV Flower Dale Feeder | 6/1/4.72 & XLPE cable 300 mm2 (240& 576A) | 1.4
|  |  |  | 11 KV Jagroti Feeder | 6/1/4.72 ACSR | 1.4
|  |  |  | 11 KV Maliana Local | 6/1/3.35 | 1.4
|  |  |  | 11 kV SJVNL feeder | 6/1/4.72 | 1.4 | Idle Feeder
36 | 33/11 kV Sub-Station Ghodpa (Mehli) | 6.3 | 4 | 11 KVBeolia Feeder | 6/1/3.35 | 1
|  |  |  | 11KV Mehli Feeder | 6/1/3.35 | 1
|  |  |  | 11 KV Kotti Feeder | 6/1/3.35 | 1
|  |  |  | 11 KV Vikas Nagar Feeder | 6/1/3.35 | 1
37 | 33/11 kV Sub-Station Ashwani Khad | 12.6 | 7.5 | 11 KV Ist Stage Feeder | 6/1/3.35 | 1.5
|  |  |  | 11 KV IIedStage Feeder | 6/1/3.35 | 1.5
|  |  |  | 11 KV Kasumpti Feeder | 6/1/3.35 | 1.5
|  |  |  | 11 KV Junga Feeder | 6/1/3.35 | 1.5
|  |  |  | 11 KV Juggo Feeder | 6/1/4.09 | 1.5 | UTRI HR Solar 500 kW
38 | 33/11 kV Sub-Station Bhattakuffer | 9.45 | 6 | 11 KV Jawar Colony Feeder | 6/1/3.35 ACSR | 1
|  |  |  | 22 KV Jagroti Feeder | ACSR (1) 6/1/3.35 (2) 6/1/2.59 sq mm | 1
|  |  |  | 22 KV Bhattakuffer Feeder | 6/1/3.35 | 1
|  |  |  | 22 KV Cemetery Feeder | 6/1/4.72 ACSR | 1
|  |  |  | 22 KV Fruit Mandi Feeder | ACSR 6/1/3.35 sq mm | 1
|  |  |  | 22 KV Mathu Colony Feeder | 6/1/3.35 ACSR | 1
39 | 33/11 kV Sub-Station Sanjauli | 6.3 | 4 | 11 kV Sanjauli Bazar | XLPE 400/300 mm2 | 1.333
|  |  |  | 11 kv St. Bedes | XLPE 400/300 mm2 | 1.333
|  |  |  | 11 kV Snowdown | XLPE 400/300 mm2 | 1.333
40 | 132/11 kV Sub-Station Kala Amb | 31.5 | 20 | 11 KV IND No-2 | ACSR 6/1/3.35mm. Sq. | 2
|  |  |  | 11 KV IND No-3 | ACSR 6/1/3.35mm. Sq. | 2
|  |  |  | 11 KV IND No-4 | ACSR 6/1/4.72mm. Sq. | 2
|  |  |  | 11 KV IND No-5 | ACSR 6/1/4.72mm. Sq. | 2
|  |  |  | 11 KV IND No-6 | ACSR 6/1/4.72mm. Sq. | 2
|  |  |  | 11 KV IND No-7 | ACSR 6/1/4.72mm. Sq. | 2
|  |  |  | 11 KV IND No-8 | ACSR 6/1/4.72mm. Sq. | 2
|  |  |  | 11 KV IND No-10 | ACSR 6/1/4.72mm. Sq. | 2
|  |  |  | 11 KV IND No-11 | ACSR 6/1/4.72mm. Sq. | 2
|  |  |  | 11 KV IND No-12 | ACSR 6/1/4.72mm. Sq. | 2
41 | 33/11 kV Sub-Station Kala Amb | 26.3 | 15.4 | 11 KV Feeder No-1 | AAAC 7/3.81mm. Sq. | 1.4
|  |  |  | 11 KV Feeder No-2 | AAAC 7/3.81mm. Sq. | 1.4
|  |  |  | 11 KV Feeder No-3 | AAAC 7/3.81mm. Sq. | 1.4
|  |  |  | 11 KV Feeder No-4 | AAAC 7/3.81mm. Sq. | 1.4
|  |  |  | 11 KV Feeder No-5 | AAAC 7/3.81mm. Sq. | 1.4
|  |  |  | 11 KV Feeder No-6 | AAAC 7/4.26mm. Sq | 1.4
|  |  |  | 11 KV Feeder No-7 | AAAC 7/3.81mm. Sq. | 1.4
|  |  |  | 11 KV Feeder No-8 | AAAC 7/3.81mm. Sq. | 1.4
|  |  |  | 11 KV Feeder No-9 | AAAC 7/3.81mm. Sq. | 1.4
|  |  |  | 11 KV Feeder No-10 | AAAC 7/4.26mm. Sq | 1.4
|  |  |  | 11 KV Feeder No-11 | XLPE Cable (3X120)mm. Sq | 1.4
42 | 33/11 kV Burma Papri | 6.3 | 3 | 11 KV Palion | AAAC 7/3.81mm. Sq. | 0.75 |  | GR Enterprises SPP (1 MW) of M/s GR Enterprises is injecting power at 33 kV level) at 33/11 kV Sub-Station Burma papri.
|  |  |  | 11 KV Power Grid | AAAC 7/3.81mm. Sq. | 0.75 | Maa Durga Shakti SPP 1 MW
|  |  |  | 11 KV Kaulawalabhood | AAAC 7/3.81mm. Sq. | 0.75
|  |  |  | 11 KV Burma Papri | AAAC 7/3.81mm. Sq. | 0.75
43 | 33/11 kV Do-Sarka Nahan | 20 | 10.4 | 11 KV Nahan-I | AAAC 7/4.26mm. Sq. | 0.72977
|  |  |  | 11 KV Nahan-II | AAAC 7/4.26mm. Sq. | 1.2086
|  |  |  | 11 KV Nahan-III | AAAC 7/4.26mm. Sq. | 1.2086
|  |  |  | 11 KV Nahan Kala Amb | AAAC 7/3.81mm. Sq. | 1.2086
|  |  |  | 11 KV Vikram Bagh | AAAC 7/3.81mm. Sq. | 1.2086
|  |  |  | 11 KV Bogeriaghat | AAAC 7/3.81mm. Sq. | 1.2086 | Sirmour SPP & Maa Balasundari SPP 1 MW each
|  |  |  | 11 KV Shambhuwala | AAAC 7/3.81mm. Sq. | 1.2086
|  |  |  | 11 KV Sarahan Bagthan | AAAC 7/3.81mm. Sq. | 1.2086
|  |  |  | 11 KV Surla Feeder | AAAC 7/4.26mm. Sq. | 1.2086
44 | 33/11 kV Substation Rajgarh | 9 | 5 | 11 KV Rajgarh | ACSR 6/1/2.59MM2 | 1
|  |  |  | 11 KV Deedag | ACSR 6/1/2.59MM2 | 1
|  |  |  | 11 KV Kheri | ACSR 6/1/2.59MM2 | 1
|  |  |  | 11 KV Habban | AAAC 7/3.15MM2 | 1
|  |  |  | 11KV Maryog | ACSR 6/1/2.59MM2 | 1 | Sharma Bros SPP 500kW
45 | 33/11 kV Substation Charna | 6.3 | 3 | 11 KV Charna Nohra | ACSR 6/1/2.59MM2 | 1
|  |  |  | 11 KV Charna Sainj -Bharari | ACSR 6/1/2.59MM2 | 1
|  |  |  | 11kV Haripur dhar | AAAC 7/3.15MM2 | 1
46 | 33/11 kV Sub-Station Haripurdhar | 3.15 | 1.8 | 11 KV Duri Kharadna | Proposed ACSR 6/1/2.59MM2 | 0.6
|  |  |  | 11 KV Badol Feeder | Proposed ACSR 6/1/2.59MM2 | 0.6
|  |  |  | 11 KV Gatta Dhar Feeder | Proposed ACSR 6/1/2.59MM2 | 0.6
47 | 33/11 kV Substation Panog | 6.3 | 3.2 | 11 KV Panjod (Panog) Feeder | AAAC 7/3.15MM2 | 0.8
|  |  |  | 11 KV Haripurdhar Feeder | ACSR 6/1/2.59MM2 | 0.8
|  |  |  | 11 KV Ronhat Feeder | ACSR 6/1/2.59MM2 | 0.8
|  |  |  | 11 KV Gatta Dhar Feeder | AAAC 7/3.15MM2 | 0.8
48 | 33/11 kV Sub-Station Kupvi | 3.2 | 2 | 11 kV Noura | 6/1/3.35 | 0.666
|  |  |  | 11 kV Samvi | 6/1/3.35 | 0.666
|  |  |  | 11 kV Malat | 6/1/3.35 | 0.666
49 | 33/11 kV Substation Kheri (Macher) | 3.15 | 2 | 11 KV Baru Sahib -Kheri Local Feeder | ACSR 6/1/2.59MM2 | 0.5
|  |  |  | 11 KV Mangarh Feeder | ACSR 6/1/2.59MM2 | 0.5
|  |  |  | 11 KV Bogdhar Feeder | AAAC 7/2.50 | 0.5
|  |  |  | 11 KV Prara Feeder | AAAC 7/3.15MM2 | 0.5
50 | 33/11 kV LWSS Gaura | 6.3 | 4 | 11 KV LWSS Gaoura 1st | ACSR 6/1/2.59MM2 | 2
|  |  |  | 11 KV LWSS Gaoura 2nd | ACSR 6/1/2.59MM2 | 2
51 | 33/11 kV Substation Sheela Bag | 3.15 | 2 | 11kV Sheela Bag Feeder | 6/1/3.35 | 0.567
|  |  |  | 11 KV Dhamandar Feeder | ACSR 6/1/2.59MM2 | 0.567
|  |  |  | 11 KV Chandol Feeder | ACSR 6/1/2.59MM2 | 0.567
|  |  |  | 11 KVShargaon Koti Feeder | ACSR 6/1/2.59MM2 | 0.567 | Jai Shrigul SPP 500kW
52 | 33/11 kV Dhaulakuan | 20 | 12 | 11 KV Kolar | AAAC 7/3.81 | 2 | KGF SPP 500kW
|  |  |  | 11 KV Rampur-1st | AAAC 7/3.81 | 2 | Shiv Shakti SPP 1 MW
|  |  |  | 11KV Majra | ACSR 6/1/2.59 | 2
|  |  |  | 11 KV Gujjar colony | AAAC 7/3.81 | 2 | NS Enterprises SPP 1 MW
|  |  |  | 11 KV Puruwala | AAAC 7/3.81 | 2
|  |  |  | 11 KV Rampur-2nd | AAAC 7/3.81 | 2
53 | 33/11 kV Dadahu | 9.45 | 3 | 11 KV Left Bank | ACSR 6/1/2.59mm. Sq | 1
|  |  |  | 11 KV Right Bank | ACSR 6/1/2.59mm. Sq | 0 | Neelkanth Mahadev SPP 1 MW, Shrikhand Mahadev SPP 2 MW
|  |  |  | 11 KV Sangrah | ACSR 6/1/2.59mm. Sq | 1
|  |  |  | 11 KV Renuka feeder | ACSR 6/1/4.72mm. Sq | 1
54 | 33/11 kV Sangrah | 3.15 | 2 | 11 KV Andheri | ACSR 6/1/2.59mm. Sq | 0.666
|  |  |  | 11 KV Rajana | ACSR 6/1/4.72mm. Sq | 0.666
|  |  |  | 11 KV Sangrah | ACSR 6/1/2.59mm. Sq | 0.666
55 | 33/11 kV Jagatpur Johron | 12.6 | 7 | 11KV Surajpur | ACSR 6/1/4.72 | 2.333
|  |  |  | 11 KV jagatpur industrial | ACSR 6/1/4.72 | 2.333
|  |  |  | 11 KV Bhagwanpur | ACSR 6/1/4.72 | 2.333 | Shiv Kripa SPP 1 MW
56 | 33/11 kV Badripur | 20 | 14 | 11KV Paonta | AAAC 7/4.26 & 120 sq. mm AB Cable | 1.4
|  |  |  | 11KV Kedarpur | AAAC 7/4.26 | 1.4
|  |  |  | 11 KV Hospital | AAAC 7/4.26 & 120 sq. mm AB Cable | 1.4
|  |  |  | 11KV Vish Karma | AAAC 7/4.26 & 120 sq. mm AB Cable | 1.4
|  |  |  | 11KV Jamaniwala | AAAC 7/4.26, 7/3.15 & ACSR 6/1/2.59 | 1.4
|  |  |  | 11KV Surajpur | AAAC 7/4.26 | 1.4
|  |  |  | 11KV Gondpur | AAAC 7/4.26 | 1.4
|  |  |  | 11KV Industrial | AAAC 7/4.26 | 1.4
|  |  |  | 11KV Devi Nagar | AAAC 7/4.26 | 1.4
|  |  |  | 11kv Himuda | AAAC 7/4.26 | 1.4
57 | 33/11 kV Old Badripur | 12.6 | 4.3 | 11KV Bata-Mandi | AAAC 7/4.26 | 3.1413
|  |  |  | 11KV Patlion | ACSR 6/1/4.72 & 6/1/2.11, AAAC 7/3.15 | 1.2209
58 | 33/11 kV GIS Paonta | 20 | 12 | 11 KV Kripalshila | AAAC 7/4.26 | 3
|  |  |  | 11 KV Bangarn Chaowk | AAAC 7/4.26 | 3
|  |  |  | 11 KV Mini Sec. | AAAC 7/4.26 | 3
|  |  |  | 11 KV Y Point | AAAC 7/4.26 | 3
59 | 33/11 kV Sataun | 12.6 | 5 | 11kv Chandni | ACSR 6/1/3.35 | 1.25 | Proposed for Augumentation. There is already injection of 11 MW in these sub-Stations.
|  |  |  | 11kv Sataun local | ACSR 6/1/3.35 | 1.25
|  |  |  | 11kv Kamrau | ASCR 6/1/3.35 | 1.25
|  |  |  | 11kv Rajban | ASCR 6/4.72 | 1.25
60 | 33/11 kV Shillai | 12.6 | 1 | 22 kV Dharuwa-Gumma | 6/1/2.59 | 0.2
|  |  |  | 11 KV Shillai Feeder | ASCR 6/1/2.59 | 0 | Pashmi SPP 500kW
|  |  |  | 11 KV IPH Feeder | AAAC 7/3.81 | 0.2
|  |  |  | 11 KV Dharwa Feeder | AAAC 7/3.81 | 0.2
|  |  |  | 11 KV Kaffota Feeder | ASCR 6/1/2.59 | 0.2
|  |  |  | 11 KV Timbi Feeder | ASCR 6/1/2.59 | 0.2
61 | 33/11 kV Rampurghat | 12.6 | 8.1 | 11KV Rampur Ghat | AAAC 7/3.81 | 1.35
|  |  |  | 11 KV Dental collage | 120 sq. mm AB Cable | 1.35
|  |  |  | 11 KV Kuja | AAAC 7/3.81 & 120 sq. mm AB Cable | 1.35
|  |  |  | 11KV Housing Board | AAAC 7/3.81 | 1.35
|  |  |  | 11KV Barotiwala | AAAC 7/3.81 | 1.35
|  |  |  | 11 KV Matraliyon | 120 sq. mm AB Cable | 1.35
62 | 33/11 kV Puruwala | 12.6 | 8.1 | 11kv Salwala | ACSR 6/1/3.35 | 1.35
|  |  |  | 11kv Bhagani | AAAC 7/4.26 | 1.35
|  |  |  | 11kv Rajpura | AAAC 7/3.15 | 1.35
|  |  |  | 11kv Khorowala | AAAC 7/3.15 | 1.35
|  |  |  | 11kv Bangran | AAAC7/3.15 | 1.35
|  |  |  | 11kv Manpur devra | AAAC 7/3.15 | 1.35
63 | 132/11 kV Sub-Station Gondpur | 31.5 | 18.05 | 11KV V-Gondpur | AAAC 7/4.26 | 2.5
|  |  |  | 11KV R-Gondpur | AAAC 7/4.26 | 2.5
|  |  |  | 11KV L- Gondpur | AAAC 7/4.26 | 2.5
|  |  |  | 11KV P- Gondpur | AAAC 7/4.26 | 1.25 | Sumurja Shakti SPP 2 MW
|  |  |  | 11KV Taruwala | AAAC 7/4.26 | 2.5
|  |  |  | 11KV Heerpur Matralion | AAAC 7/4.26 | 2.5
|  |  |  | 11KV Bhungarni | AAAC 7/4.26 6/1/2.59 | 1.8
|  |  |  | 11KV Patti Natha Singh | AAAC 7/4.26 | 2.5
64 | 66/22 kV Sub-Station Bhoktoo | 25 | 15 | 22KV BHOKTU-R/PEO FEEDER | 6/1/3.35 | 5
|  |  |  | 22KV Sub-Stn - Bhoktu | 6/1/3.35 | 5
|  |  |  | 22KV BHOKTU-PURVANI FEEDER | 6/1/3.35 | 5
65 | 66/22 kV Sub-Station Akpa | 6.3 | 4 | 22KV AKPA-SPILLOW FEEDER | 6/1/2.59,6/1/3.35 & 6/1/4.09 | 0.8
|  |  |  | 22KV AKPA-MOORANG FEEDER | 6/1/3.35 | 0.8
|  |  |  | 22KV AKPA-RIBBA FEEDER | 6/1/3.35 | 0.8
|  |  |  | 22KV AKPA-Sub Station | 6/1/3.35 | 0.8
|  |  |  | 22KV AKPA-KHARO FEEDER | 6/1/3.35 | 0.8
66 | 66/22 kV Sub-Station Pooh | 10 | 4 | 22KV POOH FEEDER | 6/1/2.59,6/1/3.35 & 6/1/4.09 | 2.0003 | Shipkila Infra SPP 500kW
|  |  |  | 22KV POOH Sub Station | 6/1/3.35 | 2.0003
|  |  |  | 22KV POOH-KAZA FEEDER | 6/1/2.59,6/1/3.35 & 6/1/4.09 | 0 | Proposed for Augumentation. Titang Hydel Power Project (.8), Rongtong Power House (2), Lingti Power House(.4)
67 | 66/22 kV Sub-Station Kotla | 41.5 | 5.68 | 22kV Maglad PH | Dog (6/7/4.72mm2) | 0
|  |  |  | 22kV Rampur | Rabbit (6/1/3.35mm2) | 0.51636 | Proposed for Augumentation. Sachi Power House
|  |  |  | 22kV Kotgad PH | Dog (6/7/4.72mm2) | 0.51636
|  |  |  | 22kV Rattanpur PH | Dog (6/7/4.72mm2) | 0.51636
|  |  |  | 22kV Jhakri | Dog (6/7/4.72mm2) | 0.51636
|  |  |  | 22kV Kinnaur | Rabbit (6/1/3.35mm2) | 0.51636
|  |  |  | 22kV Station | Rabbit (6/1/3.35mm2) | 0.51636
|  |  |  | 22kV Maglad | Dog (6/7/4.72mm2) | 0.51636
|  |  |  | 22kV Daj | Dog (6/7/4.72mm2) | 0.51636
|  |  |  | 22kv Sarahan | Rabbit (6/1/3.35mm2) | 0.51636
|  |  |  | 22kV Ganvi Ex-Press | Dog (6/7/4.72mm2) | 0.51636
|  |  |  | 22kV Rampur Ex-Press | Wolf (30/7/2.59mm2) | 0.51636
68 | 66/22 kV Sub-Station Nathpa | 30 | 6.1 | 22KV NATHPA OLD KINNAUR FEEDER | 6/1/3.35&6/1/2.59&6/1/4.72 | 0 | Proposed for Augumentation. Door Sanchar Hydro Power Pvt Ltd. (5), Rukti Power House (1.5)
|  |  |  | 22KV NATHPA NEW KINNAUR FEEDER | 6/1/3.35&6/1/2.59&6/1/4.72 | 0.67778
|  |  |  | 22KV NATHPA-CHAURA FEEDER | 6/1/3.35&6/1/2.59&6/1/4.72 | 0.67778
|  |  |  | 22KV NATHPA-NICHAR FEEDER | 6/1/3.35 | 0.67778
|  |  |  | 22KV NATHPA-KATGAON FEEDER | 6/1/3.35 | 0.67778
|  |  |  | 22KV NATHPA-SJVNL FEEDER | 6/1/4.72 | 0.67778
|  |  |  | 22KV NATHPA JP-I FEEDER | 6/1/4.72 | 0.67778
|  |  |  | 22KV NATHPA Sub-Station | 6/1/3.35 | 0.67778
|  |  |  | 22KV NATHPA JP-II FEEDER | 6/1/4.72 | 0.67778
|  |  |  | 22KV BHABA POWER HOUSE | 6/1/3.35 | 0.67778
69 | 66/22 kV Sub-Station Nogli | 20 | 6.18 | 22kV Nogli-Rampur Tie Line. | Dog (6/7/4.72mm2) | 0.7725
|  |  |  | 22kV Nogli-Rampur Old | Rabbit (6/1/3.35mm2) | 0.7725
|  |  |  | 22kV Nogli-Taklech | Rabbit (6/1/3.35mm2) | 0.7725
|  |  |  | 22kV Nogli- Bhali. | Rabbit (6/1/3.35mm2) | 0.7725
|  |  |  | 22kV Nogli Thanadhar. | Rabbit (6/1/3.35mm2) | 0.7725
|  |  |  | 22kV Nogli Dansa. | Rabbit (6/1/3.35mm2) | 0.7725
|  |  |  | 22kV LWSS Kashapat | Rabbit (6/1/3.35mm2) | 0.7725
|  |  |  | 22kV Nogli Nirmand | Rabbit (6/1/3.35mm2) | 0 | Shrikhand (.5). Himalyan (.5) Shrikhand Kailash I & II 1+1 MW
|  |  |  | 22kV Nogli Jhakatkhana (Khaneri) | Rabbit (6/1/3.35mm2) | 0.7725
70 | 66/22 kV Sub-Station Kumarsain | 20 | 10.425 | 22 kV Kotighat-Dharkandroo | 6/1/3.35mm | 0.94773
|  |  |  | 22 kV Narkanda- Shilaroo | 6/1/4.72mm | 0.94773
|  |  |  | 22KV Baragaon Feeder | ACSR 6/1/3.35 mm | 0.94773
|  |  |  | 22KV Rampur Feeder | ACSR 6/1/3.35 mm | 0.94773
|  |  |  | 22KV Kumarsain Feeder | ACSR 6/1/3.35 mm | 0.94773
|  |  |  | 22KV Narkanda Feeder | ACSR 6/1/3.35 mm | 0.94773
|  |  |  | 22KV Madhawani Feeder | ACSR 6/1/3.35 mm | 0.94773
|  |  |  | 22KV Nankhari Jahu Feeder | ACSR 6/1/3.35 mm | 0.94773
|  |  |  | 22KV Thanedhar Feeder | AAAC 7/3.81 mm | 0.94773
|  |  |  | 22KV Anni Feeder | ACSR 6/1/3.35 mm | 0.94773
|  |  |  | 22KV Adani Feeder | ACSR 6/1/4.09 mm | 0.94773
71 | 66/22 kV Sub-Station Nagan (Anni) | 20 | 4.4 | 22KV Anni Feeder | ACSR 6/1/3.35 mm | 0.73333
|  |  |  | 22 KV Khang | ACSR 6/1/3.35 mm | 0.73333
|  |  |  | 22KV Showad | ACSR 6/1/3.35 mm | 0.73333
|  |  |  | 22KV Dalash | ACSR 6/1/3.35 /AAAC/7.3.81 mm | 0.73333
|  |  |  | 22KV Himadri Power House | Dog (6/7/4.72mm2) | 0.73333
|  |  |  | 22KV Sub-Stn - Nagan | Dog (6/7/4.72mm2) | 0.73333
72 | 66/22 kV Sub-Station Samoli | 36 | 19.92 | 22 kV Sawra Kuddu HEP | 6/1/3.35 mm2 | 2.8457 | SKHEP = 111 MW
|  |  |  | 22 kV Samoli - Gangtoli - Hatkoti | 6/1/4.72mm2 | 2.8457 | Cheing HEP =1.0 MW
|  |  |  | 22 KV Feeder Chirgaon 1 | Dog-6/1/4.72 | 2.8457
|  |  |  | 22 KV Feeder Chirgaon 2 | Dog-6/1/4.72 | 2.8457
|  |  |  | 22 KV Feeder Rohru 1 (Samoli-Gangtoli) | Dog-6/1/4.72 | 2.8457
|  |  |  | 22 KV Feeder Rohru 2 (Samoli-Gangtoli) | Dog-6/1/4.72 | 2.8457
|  |  |  | 22 KV Feeder Samoli-Kansakoti | Rabbit-6/1/3.35 | 2.8457
73 | 66/22 kV Sub-Station Andhra | 6.67 | 0 | 22 kV Incomer feedeer Control Point Chirgaon | Rabbit-6/1/3.35 | 0 | Porposed for Augumentation of Cable/Conductor
|  |  |  | 22 kV Feeder Andhra-Gumma | Rabbit-6/1/3.35 | 0
74 | 66/22 kV Sub-Station Craignao (Mashobra) | 20 | 7.2 | 22 kV Tarapur | XLPE 300 mm | 1.0286
|  |  |  | 22 kV Durgapur | XLPE 300 mm | 1.0286
|  |  |  | 22 kV Kiarkoti | XLPE 300 mm | 1.0286
|  |  |  | 22 kV Sharai | XLPE 300 mm | 1.0286
|  |  |  | 22 kV AIR | XLPE 300 mm | 1.0286
|  |  |  | 22 KV Mashobra Cemetry Feeder | ACSR 6/1/4.72 | 1.0286
|  |  |  | 22kv Mashobra - Dhalli | ACSR 6/1/4.72 | 1.0286
75 | 66/22 kV Sub-Station Gumma | 36.3 | 12.568 | 22kV Gumma Basantpur Sunni | ACSR 6/1/4.72,6/1/3.35 & 6/1/2.59 | 0.73929
|  |  |  | 22kV Gumma Chaba No.2 | ACSR 30/7/2.59 mm | 0.73929
|  |  |  | 22kV Gumma Chaba No.1 | ACSR 30/7/2.59 mm | 0.73929
|  |  |  | 22 KV Gumma-KadharGhat Feeder | ACSR 6/1/4.72,6/1/3.35 & 6/1/2.59 | 0.73929
|  |  |  | 22 kV Gumma No.1 | Wolf | 0.73929
|  |  |  | 22 kV Gumma No.2 | Wolf | 0.73929
|  |  |  | 22 kV Gumma No.3 | Wolf | 0.73929
|  |  |  | 22 kV Garh-Gumma | Wolf | 0.73929
|  |  |  | 22 kV Drabla No.-1 | Wolf | 0.73929
|  |  |  | 22 kV Drabla No.-2 | Wolf | 0.73929
|  |  |  | 22 kV Chehar | Wolf | 0.73929
|  |  |  | 22 kV AIR | Wolf | 0.73929
|  |  |  | 22 kV Theog | 6/1/4.72 mm | 0.73929
|  |  |  | 22 kV Bazar | 6/1/4.72 mm | 0.73929
|  |  |  | 22 kV Express | 6/1/3.35 mm | 0.73929
|  |  |  | 22 kV Fagu | 6/1/4.72 mm | 0.73929
|  |  |  | 22 kV Matiana | 6/1/3.35mm | 0.73929
76 | 66/22 kV Sub-Station Sainj | 10 | 1.6 | 11 kV LWSS Stage-1st Feeder-1 | 6/1/4.72 mm | 0.2
|  |  |  | 11 kV LWSS Stage-1st Feeder-2 | 6/1/4.72 mm | 0.2
|  |  |  | 11 kV LWSS Stage2nd Feeder-1 | 6/1/4.72mm | 0.2
|  |  |  | 11 kV LWSS Stage2nd Feeder-2 | 6/1/4.72mm | 0.2
|  |  |  | 22 kV Pulbahal | 6//1/3.35mm | 0 | Jai Singh Thakur SPP I and II 500+500kW, Chauhan CS SPP 1 MW, Surilux SPP 500kW
|  |  |  | 22 kV Deha | 6/1/3.35mm | 0.2
|  |  |  | 22 kV Adani | 6/1/3.35mm | 0.2
|  |  |  | 22 kV Theog (Dharech) | 6/1/4.72mm | 0.2 | Dharech SPP 500kW
|  |  |  | 22 kV HPMC | 6/1/4.72mm | 0.2
77 | 66/22 kV Sub-Station Hulli | 20 | 7.2 | 22 kV Chopal (Chambi) | ACSR Cond. 6/1/4.72 | 0.72
|  |  |  | 22 kV Ghoond | 6/1/3.35mm | 0.72
|  |  |  | 22 kV Shilla Ghoond | 6/1/3.35mm | 0.72
|  |  |  | 22 kV Snai | 6/1/3.35mm | 0.72
|  |  |  | 22 kV Kiar | 6/1/3.35mm | 0.72
|  |  |  | 22 kV Theog | 6/1/3.35mm | 0.72
|  |  |  | 22 kV Marog | ACSR Cond. 6/1/4.72 | 0.72
|  |  |  | 22 kV Hulli-Kotkhai Express | 6/1/4.72mm2 | 0.72
|  |  |  | 22 kV Hulli-Bagghi Express | 6/1/4.72mm2 | 0.72 | Solar = (220 KW+80 KW)
|  |  |  | 22 kV Hulli- Gumma Mahasu Express | 6/1/3.35mm2 | 0.72
78 | 66/22 kV Sub-Station Lastadhar (Chaupal) | 12.6 | 4.536 | 22 kV Chopal | ACSR Cond. 6/1/4.72 | 1.512
|  |  |  | 22 kV J/Pull | ACSR Cond. 6/1/3.35 | 1.512
|  |  |  | 22 kV Nerwa-Deiya | ACSR Cond. 6/1/3.35 | 1.512
79 | 220/66/33/11kV Katha (Baddi) Sub-Station | 80 | 57.6 | 11 KV FEEDER NO 1 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 2 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 3 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 4 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 5 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 6 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 7 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 8 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 9 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 10 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 11 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 12 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 13 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 14 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 15 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 16 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 17 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 18 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 19 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 20 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 21 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 22 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 23 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 24 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 28 | AAAC 7/4.26 | 2.2154
|  |  |  | 11 KV FEEDER NO 29 | AAAC 7/4.26 | 2.2154
80 | 33/11 kV Sub-Station New OPD IGMC | 12.6 | 8 | 11 kV New OPD IGMC | 240sq mm XLPE cable | 4
|  |  |  | 11 kV Telecobalt | 240sq mm XLPE cable | 4
81 | 33/11 KV Palhori | 1.6 | 1 | 11 KV Palhori | AAAC 7/4.26 | 1
82 | 33/11KV Harraipur Sub-Station | 6.3 | 4 | 11KV G.Claridge | AAAC 7/4.26 | 2
|  |  |  | 11KV Barotiwala | AAAC 7/4.26 | 2
| Total | 1448.62 | 736.421 |  |  | 788.2404

## Mandi Zone
Notification of sub-station & Feeder wise surplus capacity which can be fed from RE Power Plants under Mandi Zone, Mandi.
Sr. No. | Name of Sub-Station | Transformation capacity Installed at 33/11 kV Level (MVA) | Surplus Transformation capacity available at 132/11kV, 33/11 kV & 33/22 kV Level (MW) | Details of 22 kV & 11 kV Feeders |  |  |  | Remarks
|  |  |  | No. of 22 kV & 11 kV Feeders emanating from Sub-Station | Name of Feeder | Type of Conductor | Min Rational Capacity of Feeder as per Surplus Transformation Capacity (Without Minimum Loading of Feeder) (in MW)
1 | 33/22kV Batala-Behel (Karsog) | 6.3 | 3 | 1 | 22 KV Mahunag-Churag Feeder | ACSR 6/1/2.59 MM2 | 0.75 | Jai Nag Sunani SPP 500kW
|  |  |  | 2 | 22KV Batalabehal-Seri Feeder | ACSR 6/1/2.59 MM2 | 0.75
|  |  |  | 3 | 22KV Batalabehal-Karsog Feeder | ACSR 6/1/2.59 MM2 | 0.75
|  |  |  | 4 | 22KV Batala-Behal-Chhattri feeder | ACSR 6/1/2.59 MM2 | 0.75 | Shiva SPP 1 MW
2 | 33/22kV Chhattri | 3.2 | 2.304 | 1 | 22KV Ashla | ACSR 6/1/3.35 MM2 | 0.576
|  |  |  | 2 | 22KV Chhatri | ACSR 6/1/3.35 MM2 | 0.576
|  |  |  | 3 | 22 KV Fraj | ACSR 6/1/3.35 MM2 | 0.576
|  |  |  | 4 | 22KV Chheora | ACSR 6/1/3.35 MM2 | 0.576
3 | 33/11kV Sub-Station Sundernagar | 25.2 | 7 | 1 | 11 kV BSNL | ACSR 6/1/4.72, AAAC 7/3.81,Cable 120 MM2 | 1
|  |  |  | 2 | 11 kV Jain Feeder | ACSR 6/1/3.35, ACSR 6/1/4.59,AAAC 7/3.81,AAAC 7/4.26 | 1 | Rudransh &Kamaksha SPPs 500kW each, ARV SPP 1 MW
|  |  |  | 3 | 11 kV Balh | ACSR 6/1/3.35,ACSR 6/1/4.59, ACSR 6/1/2.59,AAAC7/3.15 | 1
|  |  |  | 4 | 11 kV S-1 | ACSR 6/1/4.22, ACSR 6/1/2.59, ACSR 6/1/3.35 | 1 | Malti SPP 250kW
|  |  |  | 5 | 11 kV S-2 | ACSR 6/1/4.72 | 1
|  |  |  | 6 | 11 kV Chaugan | ACSR 6/1/4.72 | 1
|  |  |  | 7 | 11 kV BSL | Cable 120 MM2 | 1
4 | 33/22kV Sub-Station Sundernagar | 5.65 | 3 | 8 | 22 kV Chalki | ACSR 6/1/3.35, ACSR 6/1/4.59, ACSR 6/1/2.59 | 1.5 | Him Prabh Chandel 300kW
|  |  |  | 9 | 22 kV Mahadev | ACSR 6/1/2.59 & ACSR 6/1/3.35 | 1.5
5 | 33/22 kV Sub-Station Pangna | 9.45 | 2 | 1 | 22 KV Pangna-Nihri feeder | ACSR 6/1/3.35 MM2 | 0 | Bada Deo SHEP 1.5 MW, Sunrise SPP 2 Nos. 1 MW each.
|  |  |  | 2 | 22KV Pangna-Rohanda feeder | ACSR 6/1/3.35 MM2 | 0.5
|  |  |  | 3 | 22 KV Pangna-Churag Feeder | ACSR 6/1/3.35 MM2 | 0.5
|  |  |  | 4 | 22 KV Pangna-Seri Feeder | ACSR 6/1/2.11 MM2 | 0.5
|  |  |  | 5 | 22 KV Pangna-Karsog Feeder | ACSR 6/1/3.35 MM2 | 0.5
6 | 33/22 kV Sub-Station Jaidevi | 3.15 | 0.1554 | 1 | 22 kV Suki Bai | ACSR 6/1/3.35 & ACSR 6/1/2.59 | 0.03885
|  |  |  | 2 | 22 kV Ghiri | ACSR 6/1/3.35 & ACSR 6/1/2.59 | 0.03885
|  |  |  | 3 | 22 kV Kateru | ACSR 6/1/3.35 & ACSR 6/1/2.59 | 0.03885
|  |  |  | 4 | 22 kV Doldhar | ACSR 6/1/3.35 & ACSR 6/1/2.59 | 0.03885 | Sai SPP 1 MW, Shri Mahunag SPP 500 kW
7 | 33/11 kV Sub-Station Slapper | 6.3 | 3 | 1 | 11 kV HP Area-1 | AAAC 7/4.26, AAAC 7/2.59 | 0.6 | Prakash Chand & Bros SPP 700kW, Dev Hari SPP 300kW
|  |  |  | 2 | 11 kV HP Area-2 | ACSR 6/3.35, AAAC 7/2.50 & AAAC 7/3.15 | 0.6
|  |  |  | 3 | 11 kV Dehar | ACSR 6/1/4.72, AAAC 7/2.50 &AAAC 7/3.15 | 0.6
|  |  |  | 4 | 11 kV Serikothi | AAA 7/3.81 & AAAC 7/3.15 | 0.6
|  |  |  | 5 | 11 kV BBMB | Cable 120 MM2 | 0.6
8 | 33/11 kV Barsu | 6.3 | 4.536 | 1 | 11 kV Gagal | AAAC 7/3.81 & AAAC 7/3.15 | 2.1674
|  |  |  | 2 | 11 kV Barsu | AAAC 7/3.15 & AAAC 7/2.50 | 1.632
9 | 132/33/11 kV Sub-Station Ratti | 6.3 | 4.536 | 1 | 11 kV Galma | ACSR 6/1/2.59,AAAC 7/3.81 ,AAAC 7/3.15 | 1.134
|  |  |  | 2 | 11 kV Pairi | AAAC 7/4.26,AAAC 7/3.15,ACSR 6/1/2.59 | 1.134
|  |  |  | 3 | 11 kV Nerchowk | ACSR 6/1/4.04,ACSR 6/1/2.59 & AAAC 7/3.81 | 1.134
|  |  |  | 4 | 11 kV Ind. Area | AAAC 7/4.26,AAAC 7/3.15 | 1.134
10 | 33/11 kV JNGEC Sundernagar | 3.15 | 2.268 | 1 | 11 kV JNGEC | Cable 120 MM2 | 1.134
|  |  |  | 2 | 11 kV Churad | ACSR 6/1/3.35 & ACSR6/1/3.35 | 1.134
11 | 33/22kV Substation Gohar | 8.8 | 1.9008 | 1 | 22 KV Local Gohar | 6/1/3.35 | 0.4752
|  |  |  | 2 | 22 KV Gohar to Chail Chowk | 6/1/3.35 | 0.4752
|  |  |  | 3 | 22KV Gohar Sianj | 6/1/2.59 | 0.4752
|  |  |  | 4 | 22 KV Gohar Dhangiyara | 6/1/2.59 | 0.4752
12 | 33/22kV Substation Thunag | 6.3 | 1.3608 | 1 | 22 KV Bagsaid Feeder | 6/1/3.35 | 0.3402
|  |  |  | 2 | 22 KV Janjehli Feeder | 6/1/3.35 | 0.3402
|  |  |  | 3 | 22KV Thunag Feeder | 6/1/3.35 | 0.3402
|  |  |  | 4 | 22KV Shillibagi Feeder | 6/1/3.35 | 0.3402
13 | 33/22 kV Substation Janjehli | 3.15 | 2.268 | 1 | 22KV Janjehli | 6/1/3.35ACSR | 1.134
|  |  |  | 2 | 22 KV Lambathach | 6/1/3.35ACSR | 1.134
14 | 33/22kV Substation Chunahan | 12.6 | 3.5088 | 1 | 22KV Ghatta | 7/3.15 | 0.8772
|  |  |  | 2 | 22KV Baggi | 7/3.15 | 0.8772
|  |  |  | 3 | 22 KV Chunahan | 7/3.15 | 0.8772 | Randhir Kumar SPP 300kW
|  |  |  | 4 | 22KV Lohara | 6/1/3.35 | 0.8772
15 | 2*3.15 MVA,33/11 kV Sub-Station Kalkhar | 6.3 | 2.5 | 1 | 11 KV Rewalsar-Durgapur | ACSR 7/4.26,6/1/2.59 | 0.625
|  |  |  | 2 | 11 KV Sidhyani-Kothigehri | ACSR 6/1/2.59,AAAC 7/3.81 | 0.625
|  |  |  | 3 | 11 KV Leda-Kothi | AAAC 7/3.81,ACSR 6/1/2.59 | 0.625 | SMM SPP 500kW
|  |  |  | 4 | 11 KV Sarkaghat | AAAC 7/3.81 | 0.625 | Sahkari Sabha SPP 1 MW
16 | 2*6.3 MVA,33/22 kV Sub-Station Saigaloo | 12.6 | 4.336 | 1 | 22 KV Bir | 7/3.81,6/1/2.11,7/3.15,6/1/3.35 ,6/1/2.59 | 1.084
|  |  |  | 2 | 22 KV Talyahar | 6/1/3.35,7/3.81,7/3.15 | 1.084 | M/S Devesh SPP (400 KW)
|  |  |  | 3 | 22 KV Kotli | 7/4.26,6/1/3.35,6/1/2.11,7/3.15 | 1.084
|  |  |  | 4 | 22 KV Randhara | 7/4.26/,6/1/2.59,7/3.81 | 1.084 | Jai Jwala SE SPP 750kW
17 | 2X3.15 MVA Sub Station Gawali (Padhar) | 6.3 | 2 | 1 | 11KV Padhar | ACSR 6/1/2.59 | 0.5
|  |  |  | 2 | 11KV Padhar-Gumma | ACSR 6/1/2.59 | 0.5
|  |  |  | 3 | 11KV Padhar-Chohar | ACSR 6/1/2.59 | 0.5
|  |  |  | 4 | 11KV Padhar-Manglana | ACSR 6/1/2.59 | 0.5
18 | 1X3.15 MVA Sub Station Tikken (Barot) | 3.15 | 2 | 1 | 11KV Tikken-Barot | ACSR 6/1/2.11, ACSR 6/1/2.59 ACSR 6/1/3.35 | 0.5
|  |  |  | 2 | 11KV Jhatingri-Tering | ACSR 6/1/2.11, ACSR 6/1/2.59 ACSR 6/1/3.35 | 0.5
|  |  |  | 3 | 11KV Tikken-Sudhar | ACSR 6/1/2.11, ACSR 6/1/2.59 ACSR 6/1/3.35 | 0.5
|  |  |  | 4 | 11KV Chotta Bhangal | ACSR 6/1/2.11, ACSR 6/1/2.59 ACSR 6/1/3.35 | 0.5
19 | 33/22 kV Sub-Station Kataula | 3.15 | 1 | 1 | Kamand Katindi | ACSR 6/1/3.35mm,AAAC 7/3.15 mm | 0.333 | AV Traders SPP 1 MW, Virajatav SPP 0.5 MW
|  |  |  | 2 | Kataula | ACSR 6/1/3.35 mm,AAAC 7/3.15 mm | 0.333
|  |  |  | 3 | Batheri | ACSR 6/1/3.35mm,AAAC 7/3.15 mm | 0.333
20 | 2*5 MVA,33/11 kV Sub-Station Saulikhad | 10 | 4 | 1 | 11 Paddal | ACSR-6/1/3.35 | 0.9
|  |  |  | 2 | 11 KV Sauli Khad II | ACSR-6/1/4.72 | 0.9
|  |  |  | 3 | 11 KV Gutkar | ACSR-6/1/4.72 | 0.9
|  |  |  | 4 | 11 Majhwar | ACSR-6/1/4.72 | 0.4 | Kipper SPP (500 KW), NB Power Project (2MW), Maa Dhumavati SPP 250kW
|  |  |  | 5 | 11 KVBhiuli | ACSR-6/1/3.35,ACSR 6/1/4.72,3*120 SQ MM HT AB Cable | 0.9
21 | 2*6.3 MVA,33/11kV Sub-Station Samkhetar (Mandi) | 12.6 | 6 | 1 | 11 KV Jail Raod | 3*240 3 core 11 KV XLPE Cable, 3*120 sqmm HT AB Cable, ACSR 7/4.26 | 1.2
|  |  |  | 2 | 11 KV Seri | 3*240 3 core 11 KV XLPE Cable, ACSR 7/4.27 | 1.2
|  |  |  | 3 | 11 KV Hospital | 3*240 3 core 11 KV XLPE Cable, 3*120 sqmm HT AB Cable, ACSR 7/4.26 | 1.2
|  |  |  | 4 | 11 KV Samkhetar | 3*240 3 core 11 KV XLPE Cable, ACSR 7/4.27 | 1.2
|  |  |  | 5 | 11 KV Mangwain | 3*240 3 core 11 KV XLPE Cable, 3*120 sqmm HT AB Cable, ACSR 7/4.26 | 1.2 | Dyal SPP 400kW
22 | 33/11 kV Sub-Station Bijni | 6.3 | 3 | 1 | 11 Khaliyar Purani Mandi | 6/1/4.72,3*120 sq mm HT AB Cable | 0.75
|  |  |  | 2 | 11 KV Drang Dhanog | ACSR 6/1/3.35 | 0.75
|  |  |  | 3 | 11 KV Saulikhad | ACSR 6/1/3.35 | 0.75
|  |  |  | 4 | 11 KV Bari | ACSR6/1/3.35, 3*120 sqmm HT AB Cable | 0.75
23 | 33/11kV Barchhwar (Sarkaghat) | 10 | 4.2 | 1 | 11 KV Barchhwar- Rissa | 7/3/81 AAAC | 0.6 | Rup Lal SPP 500kW, Amar SPP 250 kW
|  |  |  | 2 | 11 KV Barchhwar- Sarkaghat | 7/4.26 AAAC | 0.6
|  |  |  | 3 | 11 KV Barchhwar- Dharampur | 7/3/81 AAAC | 0.6
|  |  |  | 4 | 11 KV Barchhwar- Tihra | 7/3/81 AAAC | 0.6 | Sher E Punjab 500kW, Sher E Punjab Stage-2 1 MW
|  |  |  | 5 | 11 KV Barchhwar- Gopalpur | 7/3/81 AAAC | 0.6
|  |  |  | 6 | 11 KV Barchhwar- Mohin | 7/3/81 AAAC | 0.6
|  |  |  | 7 | 11 KV Barchhwar-Maseran | 6/1/4.72 | 0.6
24 | 33/11kV Rakhota (Bhaderwar) | 3.2 | 1 | 1 | 11 KV Rakhota-Pingla | 7/3/81 AAAC+6/1/2.59ACSR | 0.25
|  |  |  | 2 | 11 KV Rakhota-Maseran | 7/3/81 AAAC | 0.25 | Richmit SPP-2 750 kW
|  |  |  | 3 | 11 KV Rakhota-Jamni | 7/4/26 AAAC+6/1/2.59ACSR | 0.25
|  |  |  | 4 | 11 KV Rakhota-Chandesh | 7/3/81 AAAC | 0.25 | Rakesh SPP 500kW
25 | 2X1.6 MVA 33/11 kV Cholthara | 3.2 | 1 | 1 | 11 KV Cholthra- Tihra | 6/1/4.72 | 0.25 | Phoenix Solar Soln SPP 1 MW
|  |  |  | 2 | 11 KV Cholthra -Sadhot | 6/1/4.72 | 0.25
|  |  |  | 3 | 11 KV Cholthra -Sarkaghat | 6/1/4.72 | 0.25
|  |  |  | 4 | 11 KV Cholthra -Sajaopiplu/Rosso | 6/1/4.72 | 0.25
26 | 2x1.6 MVA 33/11 kV Mandap | 3.2 | 2.0736 | 1 | 11 KV Mandap-Baroti | 7/3/81 AAAC | 0.6912
|  |  |  | 2 | 11 KV Mandap-Chowki/Chhatter | 7/3/81 AAAC | 0.6912
|  |  |  | 3 | 11 KV Mandap-Brang | 7/3/81 AAAC | 0.6912
27 | 2x3.15 MVA, 33/11 kV Dharampur | 6.3 | 4.0824 | 1 | 11 KV Dharampur-Kandapattan | 7/4/26 Dog | 0.5103
|  |  |  | 2 | 11 KV Dharampur -Dharampur | 7/3/81 AAAC | 0.5103
|  |  |  | 3 | 11 KV Dharampur-Richlli | 7/3/81 AAAC | 0.5103
|  |  |  | 4 | 11 KV Dharampur- Baroti | 7/3/15 AAAC | 0.5103
|  |  |  | 5 | 11KV Dharampur-Longni | 7/3/81 AAAC | 0.5103
|  |  |  | 6 | 11 KV Dharampur- Sidhpur | 7/3/81 AAAC | 0.5103
|  |  |  | 7 | 11 KV Dharampur- Bahri | 7/4/26 Dog | 0.5103
|  |  |  | 8 | 11 KV Dharampur- Gantryelu Nala | 7/4/26 Dog | 0.5103
28 | 1x3.15 MVA 33/11 kV Marhi | 3.15 | 1.8 | 1 | 11KV Marhi- Marhi Local | 6/1/3.35 | 0.6
|  |  |  | 2 | 11KV Marhi-Sakalana | 6/1/3.35 | 0.6
|  |  |  | 3 | 11KV Marhi-Kamlah | 6/1/2.59 ACSR | 0.6
29 | 1x3.15 + 1x1.6 MVA 33/11 kV Sandhole | 4.75 | 3 | 1 | 11 KV Sandhole -Sandhole | 7/3.81 AAAC & 6/1/4.72 ACSR | 0.5
|  |  |  | 2 | 11 KV Sandhole- Kujabalh | 7/3.81 AAAC & 6/1/4.72 ACSR | 0.5
|  |  |  | 3 | 11 KV Sandhole- Kothuwan | 7/3.81 AAAC & 6/1/4.72 ACSR | 0.5
|  |  |  | 4 | 11 KV Sandhole-Beri | 7/4/26 Dog | 0.5
|  |  |  | 5 | 11 KV LIS Balyali | 7/4/26 Dog | 0.5
|  |  |  | 6 | 11 KV LWSS Balla Fedeer | 7/4/26 Dog | 0.5
30 | 2x6.3 MVA 33/11 kV Bahri LIS | 12.6 | 7 | 1 | 11KV LIS Bahri-Booster Stage | 7/4/26 AAAC | 1.4515 | Not Energised yet
|  |  |  | 2 | 11KV LIS Bahri-Ist Stage | 7/4/26 AAAC | 1.4515 | Not Energised yet
|  |  |  | 3 | 11KV LIS Bahri-2nd Stage | 7/3/81 AAAC | 1.4515
|  |  |  | 4 | 11KV LIS Bahri-3rd Stage | 6/1/3.35 & 6/1/2.59 | 1.4515
|  |  |  | 5 | 11 KV LWSS Parsda Hawani Feedar | 7/4/26 AAAC | 1.4515 | Not Energised yet
31 | 33/11 kV Sub-Station Makreri | 1.6 | 1 | 1 | 11KV Makriri | ACSR 6/1/2.59 ACSR 6/1/3.35 | 0.25
|  |  |  | 2 | 11KV Makriri-Drubal | 6/1/2.11 | 0.25
|  |  |  | 3 | 11KV Makriri-Tulah | AAAC 7/4.26 AAAC 7/3.81 | 0.25
|  |  |  | 4 | 11KV Makriri-Langna | AAAC 7/4.26 AAAC 7/3.81 | 0.25
32 | 2X1.6 MVA Sub Station Bhararoo | 3.2 | 1.8 | 1 | 11KV Bhararoo-Machiyal | ACSR-6/1/3.35, AAAC 7/3.15 | 0.6
|  |  |  | 2 | 11KV Nauhli | ACSR-6/1/3.35, AAAC 7/3.15 | 0.6
|  |  |  | 3 | 11KV Gaduhi | ACSR-6/1/3.35, AAAC 7/3.15 | 0.6
33 | 1 X 4.0 MVA + 1X 2.5MVA Sub Station Lad Bharol | 6.5 | 2.504 | 1 | 11KV Lad-Bharol | AAAC 7/3.81 | 0.41733
|  |  |  | 2 | 11KV Lad Bharol-Khaddar | AAAC 7/3.81 | 0.41733
|  |  |  | 3 | 11KV Lad Bharol-Bhagair | AAAC 7/3.81 | 0.41733
|  |  |  | 4 | 11KV Lad Bharol- Pandol | AAAC 7/3.81 | 0.41733
|  |  |  | 5 | 11KV Golwan | AAAC 7/3.81 | 0.41733
|  |  |  | 6 | 11KV Simas | ACSR 6/1/2.59 | 0.41733
34 | 2 X 3.15 MVA Sub Station Chauntra | 6.3 | 4.536 | 1 | 11KV Chauntra | AAAC 7/3.81, AAAC 7/3.15, ACSR 6/1/3.35 | 1.134
|  |  |  | 2 | 11KV Chauntra-Ahju | ACSR 6/1/3.35 AAAC 7/3.15 | 1.134
|  |  |  | 3 | 11KV Chauntra-Raja | ACSR 6/1/3.35 AAAC 7/3.15 | 1.134
|  |  |  | 4 | 11KV Chauntra-Bir | ACSR 6/1/3.35 AAAC 7/3.15 | 1.134
35 | 2X2.5 MVA, 33/11kV Sub Station Bassi Power House | 5 | 1 | 1 | 11KV Shanan- Joginder Nagar | AAAC 7/4.26 | 0.2 | Maa Chatarbhuja SPP 1 MW
|  |  |  | 2 | 11KV Bassi- Joginder Nagar | AAAC 7/4.26 | 0.2 | Sri Sai SPP 1 MW
|  |  |  | 3 | 11KV Bassi-Balakrupi | AAAC 7/3.81 | 0.2 | Alok SPP 500kW
|  |  |  | 4 | 11KV Bassi Colony | ACSR 6/1/2.59 | 0.2
|  |  |  | 5 | 11KV Bassi-Majharnoo | AAAC 7/4.26 | 0.2
36 | 33/11 kV Substation Pandoh | 8.8 | 5.4 | 1 | 11Kv Local | 6/1/3.35 | 0.9
|  |  |  | 2 | 11Kv Rural | 6/1/3.35 | 0.9 | SPT SPP 1 MW
|  |  |  | 3 | 11 KV JNB Pandoh | 6/1/3.35 | 0.9
|  |  |  | 4 | 11kv Kaligarh | 6/1/2.59 | 0.9
|  |  |  | 5 | 11KV SARANDHA | 6/1/3.35 | 0.9
|  |  |  | 6 | 11 KV BBMB | 6/1/2.59 | 0.9
37 | 33/11kV Khudla | 6.3 | 0 | 1 | 11 KV Khudla- Sarkaghat | 7/3.15AAAC | 0
|  |  |  | 2 | 11 KV Khudla- Baldwara | 7/3.15AAAC | 0 | RD SPP 2 MW
|  |  |  | 3 | 11 KV Khudla- Smaila | 6/1/3.35 | 0 | Jalpa SPP 750kW
|  |  |  | 4 | 11 KV Khudla- Sulpur- Bahi | 7/3.15AAAC | 0 | Sadhwani SPP 250kW, Shivam SPP 250kW, Nadda SPP 500kW, Kapil 500kW
38 | 2*3.15 MVA Sarabai | 6.3 | 3 | 1 | 11 KV Diyar Feeder | ACSR 6/1/2.59, 6/1/3.35, 6/4.72 mm2 | 1 | Diyar SPP 250kW
|  |  |  | 2 | 11 KV Kalehli Feeder | ACSR 6/1/2.59, 6/1/3.35 | 1 | BRK Green Tech SPP 250kW
|  |  |  | 3 | 11 KV Airport Feeder | ACSR 6/1/3.35 mm2 | 1
39 | 2*6.30 MVA Bhuntar | 12.6 | 6.5 | 1 | 11 KV Hathithan Feeder | ACSR 6/1/3.35, 6/1/2.59 | 1.3
|  |  |  | 2 | 11 KV Bajaura Feeder | ACSR 6/1//4.72, 6/1/3.35 mm2, AB Cable Cable 95 mm2 | 1.3
|  |  |  | 3 | 11 KV Mohal Feeder | ACSR 6/4.72,6/1/3.35, 6/4.72+7/4.57 | 1.3 | Smile SPP 250kW, Bhutti Weavers 250kW
|  |  |  | 4 | 11 KV Bhuntar Feeder | HT AB Cable 95 mm2,70mm2,ACSR 6/1/3.35,6/4.72 mm2 | 1.3 | Tara Energy 250 kW
|  |  |  | 5 | 11 KV Shat | ACSR6/1/3.35 ,6/4.72+7/4.57, 6/1/2.59 | 1.3
40 | Kullu | 20 | 7.2 | 1 | Dhalpur-I | ACSR 6/1/3.35 | 0.65455
|  |  |  | 2 | Dhalpur-II | ACSR 6/1/3.35 | 0.65455
|  |  |  | 3 | Akhara | ACSR 6/1/3.35 | 0.65455
|  |  |  | 4 | Sarwari | ACSR 6/1/3.35 | 0.65455
|  |  |  | 5 | Gandhinagar | ACSR 6/1/3.35 | 0.65455
|  |  |  | 6 | Kolibehar | ACSR 6/1/3.35 | 0.65455
|  |  |  | 7 | Kharahal | ACSR 6/1/3.35 | 0.65455 | Indrasan Urja Power Project 250kW
|  |  |  | 8 | LIS Kharahal | ACSR 6/1/3.35 | 0.65455
|  |  |  | 9 | Babeli | ACSR 6/1/3.35 | 0.65455
|  |  |  | 10 | Lugvalley | ACSR 6/1/3.35 | 0.65455
|  |  |  | 11 | Seubag | ACSR 6/1/3.35 | 0.65455
41 | Ninu nalla | 3.2 | 2 | 1 | 11KV Diyar Feeder | Rabbit 6/1/3.35mm2 | 1
|  |  |  | 2 | 11KV Shilaharh Feeder | Rabbit 6/1/3.35mm3 | 1
42 | Nagwain | 8.15 | 5 | 1 | 11KV Garsa Feeder | Rabbit 6/1/3.35mm2 | 1.25
|  |  |  | 2 | 11KV Panarsa Feeder | Rabbit 6/1/3.35mm2 | 1.25
|  |  |  | 3 | 11KV Nagwain Feeder | Rabbit 6/1/3.35mm2 | 1.25 | Maharaja Power SPP 250kW
|  |  |  | 4 | 11KV Ropa Feeder | Rabbit 6/1/3.35mm2 | 1.25
43 | Thalout | 9.45 | 6 | 1 | 11 KV LHEP Thalout | 6/1/3.35 | 1.5
|  |  |  | 2 | 11 KV Larji- Balichowki | 6/1/3.35 | 1.5
|  |  |  | 3 | 11 KV Panjain | 6/1/3.35 | 1.5
|  |  |  | 4 | 11 KV Thachi-Jawalapur | 6/1/3.35 | 1.5 | GRT SPP 250kW
44 | Balichowki | 3.15 | 1.8 | 1 | 11KV Balichowki fdr. | ACSR 6/1/3.35 mm2, ACCC 7/3.35 mm2 | 0.6
|  |  |  | 2 | 11KV Thatibir fdr. | ACSR 6/1/3.35 mm2, ACCC 7/3.35 mm2 | 0.6
|  |  |  | 3 | 11KV Manni fdr. | ACSR 6/1/3.35 mm2, ACCC 7/3.35 mm2 | 0.6
45 | Sainj | 6.3 | 2.1 | 1 | 11 KV HPPCL | 6/1/4.72 | 0.3
|  |  |  | 2 | 11 KV NHPC-I | 6/1/4.72 & 7/3.15 | 0.3
|  |  |  | 3 | 11 KV NHPC-III | 6/1/4.72 | 0.3
|  |  |  | 4 | NHPC-II | 6/1/4.72 & 7/3.15 | 0.3
|  |  |  | 5 | 11 KV L&T | 6/1/4.72 & 7/3.15 | 0.3
|  |  |  | 6 | 11 KV Sainj-Neuli | 6/1/3.35 & 6/1/2.59 | 0.3
|  |  |  | 7 | 11 KV Sainj-Larji | 6/1/3.35 & 6/1/2.59 | 0.3
46 | Banjar | 6.3 | 4 | 1 | 11 KV Banjar fdr. | ACSR/AAAC 6/1/4.72 mm2 & 6/1/3/35 mm2 | 1
|  |  |  | 2 | 11 KV Gushaini fdr. | ACSR/AAAC 6/1/2.59 mm2 & 6/1/3/35 mm2 & off size | 1
|  |  |  | 3 | 11 KV Garagushaini | ACSR/AAAC 6/1/2.59 mm2 & off size | 1
|  |  |  | 4 | 11 KV Banjar-Balichowki fdr. | ACSR/AAAC 6/1/2.59 mm2 & off size cond, | 1
47 | Bahu | 1.6 | 1 | 1 | 11KV Khauli | ACSR/AAAC 6/1/2.59 mm2 & 6/1/3/35 mm2 & off size | 0.5
|  |  |  | 2 | 11KV Bahu | ACSR/AAAC 6/1/2.59 mm2 & 6/1/3/35 mm2 & off size | 0.5
48 | 2*3.15 MVA Jari | 6.3 | 0.3536 | 1 | 11 KV Jari | ACSR 6/1/4.72 | 0.11787 | Thuchaning SHEP 1 MW, Nazonga SHEP 0.9 MW
|  |  |  | 2 | 11 KV Manikaran | ACSR 6/1/4.72 | 0.11787
|  |  |  | 3 | 11 KV MPCL | ACSR 6/1/4.72 | 0.11787
49 | 2*1.6 MVA Barshaini | 3.2 | 0.2304 | 1 | 11 KV Barshaini | ACSR 6/1/4.72 | 0.0768
|  |  |  | 2 | 11 KV Patel | ACSR 6/1/3.35 | 0.0768 | Idle Feeder
|  |  |  | 3 | 11 KV NHPC | ACSR 6/1/3.35 | 0.0768
50 | Naggar | 10 | 5 | 1 | 11KV Sarsai Feeder | ACSR 6/1/3.35 sqmm | 1
|  |  |  | 2 | 11KV Hallan Feeder | ACSR 6/1/3.35 sqmm | 1
|  |  |  | 3 | 11KV Naggar Feeder | ACSR 6/1/3.35 sqmm | 1
|  |  |  | 4 | 11KV Raison Feeder | ACSR 6/1/3.35 sqmm | 1
|  |  |  | 5 | 11KV Baragran Feeder | ACSR 6/1/3.35 sqmm | 1
51 | Prini (Manali) | 26.3 | 10 | 1 | 11KV Old Manali Feeder | ACSR 6/1/4.72 sqmm | 1.125
|  |  |  | 2 | 11KV New Manali Feeder | ACSR 6/1/4.72 sqmm | 1.125
|  |  |  | 3 | 11KV Kanyal Feeder | ACSR 6/1/4.72 sqmm | 1.125
|  |  |  | 4 | 11KV Kalath Feeder | ACSR 6/1/4.72 & 6/1/3.35 sqmm | 1.125
|  |  |  | 5 | 11KV Rural Feeder | ACSR 6/1/4.72 sqmm | 1.125
|  |  |  | 6 | 11KV Prini Feeder | ACSR 6/1/3.35 sqmm | 1.125
|  |  |  | 7 | 11KV Jagatsukh Feeder | ACSR 6/1/3.35 sqmm | 1.125
|  |  |  | 8 | 11KV Aleo Feeder | ACSR 6/1/3.35 sqmm | 1.125
52 | Karga | 2 | 1 | 1 | Keylong | 6/1/3.35 | 0.25
|  |  |  | 2 | Darcha | 6/1/3.35 | 0.25
|  |  |  | 3 | lote | 6/1/3.35 | 0.25
|  |  |  | 4 | Karga Sissu | 6/1/3.35 | 0.25
53 | Dhundhi (Mali Thach) | 6.3 | 3 | 1 | 11 KV BRO Feeder | AB CABLE 3*95+70 MM | 1.5
|  |  |  | 2 | 11KV Dhundi Feeder | AB CABLE 3*95+70 MM | 1.5
54 | Sissu | 3.15 | 1.8144 | 1 | Sissu | 6/1/3.35 | 0.9072
|  |  |  | 2 | Bro | 6/1/3.36 | 0.9072
55 | Palchan | 6.3 | 3 | 1 | 11KV Solang Feeder | ACSR 6/1/3.35 sqmm | 0.75
|  |  |  | 2 | 11KV Burwa Feeder | ACSR 6/1/3.35 sqmm | 0.75
|  |  |  | 3 | 11KV Kothi Feeder | ACSR 6/1/3.35 sqmm | 0.75
|  |  |  | 4 | 11KV Vashisht Feeder | HT AB Cable 3*120+95 sqmm & ACSR 6/1/3.35 sqmm | 0.75
56 | Thirot | 2.5 | 1.44 | 1 | Udaipur | 6/1/3.35 | 0.48
|  |  |  | 2 | Shansha | 6/1/3.35 & 6/1.2.59 mix | 0.48
|  |  |  | 3 | Colony | 6/1/2.59 | 0.48
| Total | 393.45 | 170.5082 |  |  |  | 169.0282

## Kangra Zone
Notification of sub-station & feeder wise surplus capacity which can be fed from RE Power Plants under Kangra Zone, Dharamshala.
Sr. No. | Name of Sub-Station | Transformation capacity Installed at 33/11 kV Level (MVA) | Surplus Transformation capacity available at 132/11kV, 33/11 kV & 33/22 kV Level (MW) | Details of 22 kV & 11 kV Feeders |  |  |  |  | Remarks
|  |  |  | No. of 22 kV & 11 kV Feeders emanating from Sub-Station | Name of Feeder | Type of Conductor | Maximum Capacity of Feeder as per type of Conductor (in MW) | Min Rational Capacity of Feeder as per Surplus Transformation Capacity (Without Minimum Loading of Feeder) (in MW)
1 | 33/11 kV sub-station Kangra | 20 | 4.5 | 1 | Kangra No.1 | AAAC 7/4.26, AAAC 7/3.81, AAAC7/3.15 | 2.1674 | 0.5
|  |  |  | 2 | Kangra No.2 | AAAC 7/4.26 | 3.1413 | 0.5
|  |  |  | 3 | Old Rajol | ACSR 6/1/2.59 | 1.5638 | 0.5
|  |  |  | 4 | Rajol Express | AAAC 7/4.26 | 3.1413 | 0.5
|  |  |  | 5 | Tiara | AAAC 7/3.81,AAAC 7 /3.15 | 2.1674 | 0.5
|  |  |  | 6 | Mandal | AAAC 7/3.81 | 2.7298 | 0.5
|  |  |  | 7 | 1G/Daulatpur | AAAC 7/4.26,AAAC 7/3.15 | 2.1674 | 0.5
|  |  |  | 8 | 11 KV Serathana | AAAC 7/3.81, AAAC 7/3.15 | 2.1674 | 0.5
|  |  |  | 9 | Tanda Daulatpur | AAAC 7/3.81, AAAC7/3.15 | 2.1674 | 0.5
2 | 33/11kV Tanda | 12.6 | 3.1752 | 1 | 11 KV Main Hospital | XPLE 3-CORE 400 | 5.9259 | 0.3528
|  |  |  | 2 | 11 KV Tanda-Paraclinic | XPLE 3-CORE 70MM &35 mm2 | 1.5912 | 0.3528
|  |  |  | 3 | 11 KV SSB | XPLE 3-CORE 400 & 95 mm2 | 2.7709 | 0.3528
|  |  |  | 4 | 11 KV Anatomy | XPLE 3-CORE 400 | 5.9259 | 0.3528
|  |  |  | 5 | 11 KV TBS Local Tanda | XPLE 3-CORE 70MM | 2.332 | 0.3528
|  |  |  | 6 | 11 KV WSS - Tanda | XPLE 3-CORE 70MM &95 mm2 | 2.332 | 0.3528
|  |  |  | 7 | 11 KV Tanda-Serathana | 7/3.81,7/3.15,6/1/2.59 and off size | 1.5638 | 0.3528
|  |  |  | 8 | 11 KV Tanda - Samloti | 7/3.81,7/3.15,6/1/2.59 and off size | 1.5638 | 0.3528
|  |  |  | 9 | 11 KV Tanda Daulatpur | 7/3.81,7/3.15,6/1/2.59 and off size | 1.5638 | 0.3528
3 | 33/11kV Nagrota Bagwan | 12.6 | 3.1752 | 1 | 11 KV Nagrota | AAAC 7/3.15 mm2 Off size | 2.1674 | 0.4536
|  |  |  | 2 | 11 KV Express | AB Cable 95mm2 | 3.155 | 0.4536
|  |  |  | 3 | 11 KV Industrial Estate | AAAC 7/3.15 mm2 | 2.1674 | 0.4536
|  |  |  | 4 | 11 KV Pathiar | AAAC 7/3.81, 7/3.15, 7/4.26 mm2 | 2.1674 | 0.4536
|  |  |  | 5 | 11 KV Nagrota-Samloti | AAAC 7/3.81, 7/3.15, 7/4.26 mm3 | 2.1674 | 0.4536
|  |  |  | 6 | 11 KV F.C.U | AAAC 7/3.15 mm2 | 2.1674 | 0.4536
|  |  |  | 7 | 11 KV Massal | AAAC 7/3.81 & 7/3.15, mm2 | 2.1674 | 0.4536
4 | 33/11kV Massal | 3.15 | 0 | 1 | 11 KV Engg. Collage | AAAC 7/3.15 mmsq | 2.1674 | 0
|  |  |  | 2 | 11 KV B. Pharmacy | AAAC 7/3.15 mmsq | 2.1674 | 0
|  |  |  | 3 | 11 KV Ohlari | AAAC 7/3.15 mmsq | 2.1674 | 0
5 | 33/11 kV Kothian | 3.2 | 1 | 1 | 11KV Kothian | 7/3.81,7/3.15,6/1/2.59 and off size | 1.5638 | 0.25
|  |  |  | 2 | 11KV Sarotri | 7/3.81,7/3.15,6/1/2.59 and off size | 1.5638 | 0.25
|  |  |  | 3 | 11KV Radh | 7/3.81,7/3.15,6/1/2.59 and off size | 1.5638 | 0.25
|  |  |  | 4 | 11KV Sadoon | 7/3.81,7/3.15,6/1/2.59 and off size | 1.5638 | 0.25
6 | 33/11 kV Sub-Station Baroh | 5 | 1.1375 | 1 | 11KV Kandi | AAAC 7/3.15 & 7/3.10mm2 off size | 2.1674 | 0.2275
|  |  |  | 2 | 11KV Sadoon | AAAC 7/3.15 & 7/3.10mm2 off size | 2.1674 | 0.2275
|  |  |  | 3 | 11KV Busal | AAAC 7/3.15 & 7/3.10mm2 off size | 2.1674 | 0.2275
|  |  |  | 4 | 11KV Sunhi | AAAC 7/3.15 & 7/3.10mm2 off size | 2.1674 | 0.2275
|  |  |  | 5 | 11KV Kothian | AAAC 7/3.15 & 7/3.10mm2 off size | 2.1674 | 0.2275
7 | 33/11 kV Sub-Station Cheb | 3.2 | 0.8064 | 1 | Jayanti Bihar | AAAC 7/4.26 | 3.1413 | 0.4032
|  |  |  | 2 | Kangra Mandir | AAAC 7/4.26 | 3.1413 | 0.4032
8 | 33/11 kV Sub-Station Darkata | 6.3 | 1.02 | 1 | Nandlu | ACSR 6/1/2.11,AAAC 7/3.15 | 1.2209 | 0.17
|  |  |  | 2 | Ranital | AAAC 7/4.26, ACSR 6/1/2.59 | 1.5638 | 0.17
|  |  |  | 3 | Daulatpur | AAAC 7/4.26, AAAC 7/3.81 | 2.7298 | 0.17
|  |  |  | 4 | Bane di Hatti | AAAC 7/3.81, AAAC 7/3.15,AAAC 6/1/2.59 | 1.5638 | 0.17
|  |  |  | 5 | Darkata | ACSR 6/1/2.11,ACSR 6/1/2.59, AAAC 7/3.15 | 1.2209 | 0.17
|  |  |  | 6 | Gahlian | AAAC 7/4.26, AAAC 7/3.81,ACSR 6/1/2.59 | 1.5638 | 0.17
9 | 33/11 kV Sub-Station Rajol | 6.3 | 1.5876 | 1 | 11 KV Rajol | 6/1/3.35 & off size cond. | 2.1536 | 0.3969
|  |  |  | 2 | 11 KV Bhoi | AAAC 7/3.15 | 2.1674 | 0.3969
|  |  |  | 3 | 11KV Baintlu | ACSR 6/1/3.35& off size | 2.1536 | 0.3969
|  |  |  | 4 | 11 KV Makroti | ACSR 6/1/3.35& off size | 2.1536 | 0.3969
10 | 33/11 kV Sub-Station Sidhpur | 20 | 4 | 1 | 11 KV D/shala | AAAC7/3.15 mm2 | 2.1674 | 0.44
|  |  |  | 2 | 11 KV Dari | AAAC7/3.81 mm2 | 2.7298 | 0.44
|  |  |  | 3 | 11 KV D/shala Cantt | AAAC7/3.15 mm2 | 2.1674 | 0.44
|  |  |  | 4 | 11 KV Khaniara | AAAC7/3.81 mm2, 28.221 KM & AAAC7/3.81 mm2 | 2.7298 | 0.44
|  |  |  | 5 | 11 KV Yol | AAAC7/3.81 mm2 | 2.7298 | 0.44
|  |  |  | 6 | 11 KV Barwala | AAAC7/3.15 mm2 | 2.1674 | 0.44
|  |  |  | 7 | 11 KV 53 Miles | AAAC7/3.15 mm2 | 2.1674 | 0.44
|  |  |  | 8 | 11 KV Vidhan-sabha | AB Cable 3*95 mm2 | 3.155 | 0.44
|  |  |  | 9 | 11 KV Hodal | AAAC7/3.15 mm2 | 2.1674 | 0.44
11 | 33/11 kV Sub-Station MES Yol | 12.6 | 3.1752 | 1 | 11 KV MES | AAAC7/3.15 mm2 | 2.1674 | 2.1674
12 | 33/11 kV Sub-Station Jadrangal | 3.2 | 0.8064 | 1 | 11 KV Chamunda | AAAC 7/3.81 & 7/3.15, mm2,7/4.26mm2 | 2.1674 | 0.2688
|  |  |  | 2 | 11 KV Kardiana | AAAC 7/3.81 & 7/3.15, mm2,7/4.26mm2 | 2.1674 | 0.2688
|  |  |  | 3 | 11 KV Tang | AAAC 7/3.81 & 7/3.15, mm2,7/4.26mm2 | 2.1674 | 0.2688
13 | 33/11 kV Sub-Station Nagri | 6.3 | 1.5876 | 1 | 11KV Rakh | AAAC 7/3.15MmSQ. | 2.1674 | 0.31752
|  |  |  | 2 | 11KV nagri | AAAC 7/3.15MmSQ. | 2.1674 | 0.31752
|  |  |  | 3 | 11KV Bindraban | AAAC 7/3.15MmSQ. and AAAC 7/3.81MmSQ. | 2.1674 | 0.31752
|  |  |  | 4 | 11KV gopalpur | AAAC 7/3.15MmSQ. | 2.1674 | 0.31752
|  |  |  | 5 | 11KV lahla | AAAC 7/3.15MmSQ. | 2.1674 | 0.31752
14 | 33/11 kV Sub-Station Dehra | 12.6 | 2.6 | 1 | 11 KV Dehra | ACSR 6/1/2.11 | 1.2209 | 0.65
|  |  |  | 2 | 11 KV Khabli | ACSR 6/1/2.11 & AAAC 7/3.15 | 1.2209 | 0.65
|  |  |  | 3 | 11 KV Gummer | ACSR 6/1/2.11 & AAAC 7/3.15 | 1.2209 | 0
|  |  |  | 4 | 11 KV Kundli Har | ACSR 6/1/2.11 & AAAC 7/3.15 | 1.2209 | 0
|  |  |  | 5 | 11 KV Dhaliara | ACSR 6/1/2.59 | 1.5638 | 0.65
|  |  |  | 6 | 11 KV Pragpur | ACSR 6/1/2.59 | 1.5638 | 0.65
15 | 33/11 kV Sub-Station Haripur | 3.2 | 2.304 | 1 | 11 KV Haripur | AAAC 7/3.15 & 7/3.81 | 2.1674 | 0.384
|  |  |  | 2 | 11 KV Gathutar | ACSR 6/1/2.11 & AAAC 7/3.15 | 1.2209 | 0.384
|  |  |  | 3 | 11 KV Guler | ACSR 6/1/2.11 & AAAC 7/3.15 | 1.2209 | 0.384
|  |  |  | 4 | 11 KV Kherian | ACSR 6/1/2.11 & 6/1/3.35 | 1.2209 | 0.384
|  |  |  | 5 | 11 KV Bilaspur | ACSR 6/1/2.11 & AAAC 7/3.15 | 1.2209 | 0.384
|  |  |  | 6 | 11 KV Bankhandi | ACSR 6/1/2.11 & AAAC 7/2.50 | 1.2209 | 0.384
16 | 33/11 kV Sub-Station Nagrota Surian | 6.3 | 3.5 | 1 | Nagrota Surian | ACSR 6/1/3.35 & 6/1/2.59 | 1.5638 | 0.7
|  |  |  | 2 | Katora | ACSR 6/1/3.35 & 6/1/2.59 | 1.5638 | 0.7
|  |  |  | 3 | Barial | ACSR 6/1/3.35 & 6/1/2.59 | 1.5638 | 0.7
|  |  |  | 4 | G/Jarot | AAAC-7/3.15, ACSR-6/1/2.59 &6/1/3.35 mm | 1.5638 | 0.7
|  |  |  | 5 | Masroor | ACSR 6/1/3.35 & 6/1/2.59 | 1.5638 | 0.7
17 | 33/11 kV Sub-Station Lammi Pukhar | 3.2 | 0.68 | 1 | 11 KV Dhanotu Balla | AAAC7/3.15, ACSR 6/1/2.59 | 1.5638 | 0.17
|  |  |  | 2 | 11 KV Barwara | AAAC7/3.15, ACSR 6/1/2.59 | 1.5638 | 0.17
|  |  |  | 3 | 11 KV Karoa | AAAC7/3.15, ACSR 6/1/2.59,ACSR 6/1/2.11 | 1.2209 | 0.17
|  |  |  | 4 | 11 KV Dhaliara-1 | AAAC7/3.15, ACSR 6/1/2.59,ACSR 6/1/2.11 | 1.2209 | 0.17
18 | 33/11 kV Sub-Station Dada Sibba | 5 | 2.2 | 1 | 11 KV Dada-Siba | ACSR 7/3.81 | 2.7298 | 0.55
|  |  |  | 2 | 11 KV Suel | ACSR 7/3.81 & OFF Size | 2.7298 | 0.55
|  |  |  | 3 | 11 KV Badhal | ACSR 7/3.81 | 2.7298 | 0.55
|  |  |  | 4 | 11 KV Jour bar | ACSR 7/3.81, AAAC7/3.15 | 2.1674 | 0.55
19 | 33/11 kV Sub-Station Paragpur | 6.3 | 2 | 1 | 11 KV Pragpur | ACSR 7/3.81, AAAC7/3.15, ACSR 6/1/2.59 | 1.5638 | 0.4
|  |  |  | 2 | 11 KV Garli | AAAC7/3.15, ACSR 6/1/2.59,ACSR 6/1/2.11 | 1.2209 | 0.4
|  |  |  | 3 | 11 KV Nehran Pukher | AAAC 7/3.15,ACSR 6/1/2.59 | 1.5638 | 0.4
|  |  |  | 4 | 11 KV Kaloha | ACSR 7/3.81, AAAC7/3.15 | 2.1674 | 0.4
|  |  |  | 5 | 11 KV Shantla | ACSR 7/3.81, AAAC7/3.15 | 2.1674 | 0.4
20 | 33/11 kV Sub-Station Bithloo | 6.3 | 1.6 | 1 | 11 KV Charri | 7/3.15, 7/2.0 | 1.2346 | 0.4
|  |  |  | 2 | 11 KV Local | ACSR 7/2.0 | 1.2346 | 0.4
|  |  |  | 3 | 11 KV Adit | ACSR 7/2.0 | 1.2346 | 0.4
|  |  |  | 4 | 11KV Cantt | 7/3.15 | 2.1674 | 0.4
21 | 33/11 kV Sub-Station Shahpur | 12.6 | 3.5 | 1 | 11KV Shahpur Feeder | ACSR 6/1/2.59mm | 1.5638 | 1
|  |  |  | 2 | 11KV Darini Feeder | ACSR 6/1/2.59mm | 1.5638 | 1
|  |  |  | 3 | 11KV Kotla Feeder | ACSR 6/1/2.59mm | 1.5638 | 1
|  |  |  | 4 | 11KV Harnera Feeder | ACSR 6/1/2.59mm | 1.5638 | 0.5
22 | 33/11 kV Sub-Station Lunj | 4.1 | 0 | 1 | 11KV Lapiana Harchakian Feeder | ACSR 6/1/2.59mm | 1.5638 | 0
|  |  |  | 2 | 11KV Lunj -Saproo | acsr 6/1/2.59 | 1.5638 | 0
|  |  |  | 3 | 11 KV Badkawaloo | AAAC7/3.15mm2 & ACSR6/1/2.59mm2 | 1.5638 | 0
|  |  |  | 4 | 11KV Salol | AAAC 7/4.26 mm | 3.1413 | 0
23 | 33/11 kV Sub-Station Kalapul | 20 | 3 | 1 | 11 KV Kotwali Bazar | 7/4.26,AB cable 240sq.mm | 3.1413 | 0.428
|  |  |  | 2 | 11 KV Kacchari Adda | 6 /1/3.35 mmsq | 2.1536 | 0.428
|  |  |  | 3 | 11 K Education Board | 7/4.26&7/3.81mm sq | 2.7298 | 0.428
|  |  |  | 4 | 11 KV Shyam Nager | Underground 240&120sq.mm | 3.155 | 0.428
|  |  |  | 5 | 11 KV Mcleodganj | AAAC 7/3.15mm sq | 2.1674 | 0.428
|  |  |  | 6 | 11 KV Sudher | AAAC 7/3.15mm sq | 2.1674 | 0.428
|  |  |  | 7 | 11 KV Roopway | XLPE Cable 185 mmsq | 3.9781 | 0.428
24 | 33/11 kV Sub-Station Tota rani | 6.3 | 2 | 1 | 11 KV Totarani-Bhagsu | AAAC 7/3.15 | 2.1674 | 0.4
|  |  |  | 2 | 11 KV Totarani-Naddi | AAAC 7/3.15 | 2.1674 | 0.4
|  |  |  | 3 | 11 KV Totarani-Satobary | AAAC 7/3.15mmsq | 2.1674 | 0.4
|  |  |  | 4 | 11 KV Totarani-M/ganj | AAAC 7/3.15 mmsq | 2.1674 | 0.4
25 | 33/11 kV Sub-Station Chadiar | 4.15 | 2.488 | 1 | Tanchi Chadhiar Mungal | ACSR 6/1/3.35 mm2 | 2.1536 | 0.4976
|  |  |  | 2 | Tanchi Sansai-Sari | ACSR 6/1/3.35 mm2 | 2.1536 | 0.4976
|  |  |  | 3 | Tanchi Changan | ACSR 6/1/2.11 mm2 | 1.2209 | 0.4976
|  |  |  | 4 | Tanchi Dagoh | ACSR 6/1/3.35 mm2 | 2.1536 | 0.4976
|  |  |  | 5 | Tanchi Bhulana Ashapuri | AAAC 7/3.15 mm2 + ACSR 6/1/2.11 mm2 | 1.2209 | 0.4976
26 | 33/11 kV Sub-Station Chobin | 2.5 | 1.8 | 1 | Pirh-Kunni | ACSR 6/1/3.35 mm2 | 2.1536 | 0.9
|  |  |  | 2 | Mahankal | ACSR 6/1/3.35 mm2 + 6/1/2.11mm2 | 1.2209 | 0.9
27 | 33/11 kV Sub-Station Jaisinghpur | 6.3 | 4.536 | 1 | 11 kV Harsi Sanghol | 7/3.81& 6/1/3.35 | 2.1536 | 0.9072
|  |  |  | 2 | 11kv Chadiar | 7/3.81& 6/1/3.35 | 2.1536 | 0.9072
|  |  |  | 3 | 11kv Kosri | 7/3.81& 6/1/3.35 | 2.1536 | 0.9072
|  |  |  | 4 | 11kv Jaisinghpur | 7/3.81 | 2.7298 | 0.9072
|  |  |  | 5 | 11kv Lambagaon | 7/4.26 & 7/3.81 | 2.7298 | 0.9072
28 | 33/11 kV Sub-Station Kanghain | 6.3 | 4.536 | 1 | 11KV Lambagaon Skoh | 7/3.81 | 2.7298 | 1.512
|  |  |  | 2 | 11KV Pump House | 7/3.81 | 2.7298 | 1.512
|  |  |  | 3 | 11KV Thambu Mahadev | 7/3.81 | 2.7298 | 1.512
29 | 33/11 kV Sub-Station Lahru-Dadu | 3.2 | 1.354 | 1 | 11KV Alampur | 7/3.81 | 2.7298 | 0.3385
|  |  |  | 2 | 11KV Balakrupi | 7/3.81 | 2.7298 | 0.3385
|  |  |  | 3 | 11KV Pihri Kauna | 7/3.81 | 2.7298 | 0.3385
|  |  |  | 4 | 11KV Bhallundar | 7/3.81 | 2.7298 | 0.3385
30 | 33/11 kV Sub-Station Thural | 6.3 | 4.036 | 1 | 11kV Kauna Bachhwai | 7/3.81 | 2.7298 | 0.67267
|  |  |  | 2 | 11kV Local Thural | 7/3.81 | 2.7298 | 0.67267
|  |  |  | 3 | 11kV bairghatta | 7/3.81 | 2.7298 | 0.67267
|  |  |  | 4 | 11kV Moondhi daroh | 7/3.81 | 2.7298 | 0.67267
|  |  |  | 5 | 11kV Haldra Kauna | 7/3.81 | 2.7298 | 0.67267
|  |  |  | 6 | 11kV Garh | 7/3.81 | 2.7298 | 0.67267
31 | 33/11 kV Sub-Station Dehan | 12.6 | 5 | 1 | 11kV Palampur | AAAC 7/4.26mm2 | 3.1413 | 1
|  |  |  | 2 | 11kV Khaira | 6/1/3.35mm2 | 2.1536 | 1
|  |  |  | 3 | 11kV Bhawarna | AAAC 7/2.50mm2, 7/3.81mm2, AAAC 7/3.15mm2 | 1.6324 | 1
|  |  |  | 4 | 11kV HPKVV | AAAC 7/3.15MmSQ. | 2.1674 | 1
|  |  |  | 5 | 11kV Dehan | AAAC 7/3.15MmSQ. | 2.1674 | 1
32 | 33/11 kV Sub-Station Kural | 7.3 | 2.2 | 1 | 11 KV Daroh | AAAC 7/4.26mm2, 7/3.81mm2, AAAC 7/3.15mm2 & 6/1/2.59mm2 etc | 1.5638 | 0.55
|  |  |  | 2 | 11 KV Dheera | AAAC 7/4.26mm2, 7/3.81mm2, AAAC 7/3.15mm2 & 6/1/2.59mm2 etc | 1.5638 | 0.55
|  |  |  | 3 | 11 KV Kahanphat | AAAC 7/4.26mm2, 7/3.81mm2, AAAC 7/3.15mm2 & 6/1/2.59mm2 etc | 1.5638 | 0
|  |  |  | 4 | 11 KV Panapar | 7/3.81mm2, AAAC 7/3.15mm2 & 6/1/2.59mm2 etc | 1.5638 | 0.55
|  |  |  | 5 | 11 KV Jharet | 7/3.81mm2, AAAC 7/3.15mm2 & 6/1/2.59mm2 etc | 1.5638 | 0.55
33 | 33/11 kV Sub-Station Nagni | 3.15 | 0 | 1 | 11KV Garh Feeder | 7/3.81 | 2.7298 | 0
|  |  |  | 2 | 11 KV Balota Feeder | 7/3.81 | 2.7298 | 0
|  |  |  | 3 | 11 KV Purba Moondhi | 7/4.26 | 3.1413 | 0
34 | 33/11 kV Sub-Station Khaira | 6.3 | 2.5 | 1 | 11kV Maniara | AAAC 7/3.81 (80MM2) | 2.7298 | 1
|  |  |  | 2 | 11kV Jalag | AAAC 7/3.81 (80MM2) | 2.7298 | 1
|  |  |  | 3 | 11kV LIS Khaira | AAAC 7/3.81 (80MM2) | 2.7298 | 0.5
35 | 33/11 kV Sub-Station Patti | 6.3 | 4.536 | 1 | Panchrukhi | AAAC 7/3.81mm2 | 2.7298 | 1.512
|  |  |  | 2 | Tatehal | AAAC 7/3.15 mm2 + ACSR 6/1/2.59 mm2 | 1.5638 | 1.512
|  |  |  | 3 | Ghar | AAAC 7/3.15 mm2 + ACSR 6/1/2.59 mm2 | 1.5638 | 1.512
36 | 33/11 kV Sub-Station Maranda | 20 | 10.72 | 1 | 11 KV Sarkari Sidhpur | 7/3.15 | 2.1674 | 1.365
|  |  |  | 2 | 11 KV Bandla | 7/3.15 | 2.1674 | 1.1674
|  |  |  | 3 | 11 KV Parour Sullah | 7/3.15 | 2.1674 | 1.365
|  |  |  | 4 | 11 KV HPKVV | 7/3.81 | 2.7298 | 1.365
|  |  |  | 5 | 11 KV Ghuggar | 7/4.26 | 3.1413 | 1.365
|  |  |  | 6 | 11 KV Maranda | 7/3.15 | 2.1674 | 1.365
|  |  |  | 7 | 11 KV MES | 7/3.81 | 2.7298 | 1.365
|  |  |  | 8 | 11 KV Rajpur | 7/3.15 | 2.1674 | 1.365
37 | 33/11 kV Sub-Station Darang | 3.2 | 1.8432 | 1 | 11 KV Parour | 7/3.81 | 2.7298 | 0.4608
|  |  |  | 2 | 11 KV Ghanetta | 7/3.15 | 2.1674 | 0.4608
|  |  |  | 3 | 11 KV Darang | 7/3.15 | 2.1674 | 0.4608
|  |  |  | 4 | 11 KV Rajhoon | 7/3.81 | 2.7298 | 0.4608
38 | 33/11 kV Sub-Station Baijnath | 25 | 4.5 | 1 | Baijnath | AAAC 7/3.15, 7/3.81 + ACSR 6/1/3.35 mm2 | 2.1536 | 0.5
|  |  |  | 2 | Uttrala | ACSR 6/1/3.35 mm2 + 6/1/2.11mm2 | 1.2209 | 0.5
|  |  |  | 3 | Sansal | AAAC 7/2.50 mm2 +ACSR 6/1/2.59 mm2 | 1.5638 | 0.5
|  |  |  | 4 | Bir-Express | AAAC 7/4.26 mm2 | 3.1413 | 0.5
|  |  |  | 5 | Kudail Express | ACSR 6/1/2.59 mm2 + 6/1/3.35 mm2 | 1.5638 | 0.5
|  |  |  | 6 | Chobin-Express | ACSR 6/1/3.35 mm2 | 2.1536 | 0.5
|  |  |  | 7 | Alhilal | AAAC 7/3.15 mm2 + 7/3.81 mm2 + ACSR 6/1/3.35 mm2 | 2.1536 | 0
|  |  |  | 8 | MES | ACSR 6/1/2.59 mm2 | 1.5638 | 0.5
|  |  |  | 9 | Paprola | ACSR 6/1/3.35 mm2 | 2.1536 | 0.5
|  |  |  | 10 | Majehrna | AAAC 7/3.15 mm2 + 7/3.81 mm2 + ACSR 6/1/3.35 mm2 | 2.1536 | 0.5
39 | 33/11 kV Sub-Station Tanda | 6.3 | 2.268 | 1 | 11 KV MES | AAAC 7/3.15 | 2.1674 | 0.567
|  |  |  | 2 | 11 KV Bus Stand | AAAC 7/3.15 | 2.1674 | 0.567
|  |  |  | 3 | 11 KV Sai Garden | AAAC 7/3.15 | 2.1674 | 0.567
|  |  |  | 4 | 11 KV Hospital | AAAC 7/3.15 | 2.1674 | 0.567
40 | 33/11 kV Sub-Station Holta | 6.3 | 2 | 1 | 11 KV Chandpur | AAAC 7/3.15 | 2.1674 | 0.5
|  |  |  | 2 | 11 KV HPKVV | AAAC 7/3.15 | 2.1674 | 0.5
|  |  |  | 3 | 11 KV MES | AAAC 7/3.15 | 2.1674 | 0.5
|  |  |  | 4 | 11 KV Tanda Rajpur | AAAC 7/3.15 | 2.1674 | 0.5
41 | 33/11 kV Sub-Station Paprola | 6.3 | 2.268 | 1 | Ayurverdic | AAAC 7/3.15 mm2 + ACSR 6/1/2.59 mm2 | 1.5638 | 0.756
|  |  |  | 2 | JNV | AAAC 7/3.15 mm2 + ACSR 6/1/2.59 mm2 | 1.5638 | 0.756
|  |  |  | 3 | Paprola khas | AAAC 7/3.15 mm2 + ACSR 6/1/2.59 mm2 | 1.5638 | 0.756
42 | 33/11 kV, Sub-Station Bathri | 4 | 2.1 | 1 | 11KV Bathri | ACSR 6/1/3.35 | 2.1536 | 0.7
|  |  |  | 2 | 11 KV Devi Dehra | ACSR 6/1/3.35 | 2.1536 | 0.7
|  |  |  | 3 | 11 KV Chohra | ACSR 6/1/3.35 | 2.1536 | 0.7
43 | 33/11 kV,2x5 MVA Sub-Station Dalhousie | 10 | 6 | 1 | Microwave | 6 /1/3.35 mmsq | 2.1536 | 0.5
|  |  |  | 2 | Sadar | 6 /1/3.35 mmsq | 2.1536 | 0.5
|  |  |  | 3 | Baloon | 6 /1/3.35 mmsq | 2.1536 | 0.5
|  |  |  | 4 | Manimahesh | 6 /1/3.35 mmsq | 2.1536 | 0.5
|  |  |  | 5 | City | 6 /1/3.35 mmsq | 2.1536 | 0.5
|  |  |  | 6 | Bakrota | 6 /1/3.35 mmsq | 2.1536 | 0.5
|  |  |  | 7 | Rural | 6 /1/3.35 mmsq | 2.1536 | 0.5
|  |  |  | 8 | Banikhet | 6 /1/3.35 mmsq | 2.1536 | 0.5
|  |  |  | 9 | Chamera | 6 /1/3.35 mmsq | 2.1536 | 0.5
|  |  |  | 10 | Motitibba | 6 /1/3.35 mmsq | 2.1536 | 0.5
|  |  |  | 11 | Dainkund | 6 /1/3.35 mmsq | 2.1536 | 0.5
|  |  |  | 12 | Cantt | 6 /1/3.35 mmsq | 2.1536 | 0.5
44 | 33/11 Kv,2x1.6 MVA Sub-Station Bhalaie | 3.2 | 2.304 | 1 | 11 KV Bhalaie | 6/1/2.59 mm sq and 6/1/3.35 | 1.5638 | 0.576
|  |  |  | 2 | 11 KV Manjhali | 6/1/2.59 mm sq and 6/1/3.35 | 1.5638 | 0.576
|  |  |  | 3 | 11KV Salwan | 6/1/2.59 mm sq and 6/1/3.35 | 1.5638 | 0.576
|  |  |  | 4 | 11 KV Wangal | 6/1/2.59 mm sq and 6/1/3.35 | 1.5638 | 0.576
45 | 33/11KV 2X3.15 Sub-Station Koti | 6.3 | 3.536 | 1 | 11 kV Local Chakloo | 61/3.35, 6/1/2.59 | 1.5638 | 0.884
|  |  |  | 2 | 11 kV Pukhri | 61/3.35, 6/1/2.59 | 1.5638 | 0.884
|  |  |  | 3 | 11 kV Kalhel | 61/3.35, 6/1/2.59 | 1.5638 | 0.884
|  |  |  | 4 | 11 kV Masroond | 61/3.35, 6/1/2.59 | 1.5638 | 0.884
46 | 33/11 Kv,2x1.6 MVA Sub-Station . Salooni | 3.2 | 1.2 | 1 | 11 KV Sundla | 6/1/2.59 mm sq and 6/1/3.35 | 1.5638 | 0.2
|  |  |  | 2 | 11 KV Diur | 6/1/2.59 mm sq and 6/1/3.35 | 1.5638 | 0.2
|  |  |  | 3 | 11 KV Salooni | 6/1/2.59 mm sq and 6/1/3.35 | 1.5638 | 0.2
|  |  |  | 4 | 11 KV Banjal | 6/1/2.59 mm sq and 6/1/3.35 | 1.5638 | 0.2
|  |  |  | 5 | 11 KV Bhandal | 6/1/2.59 mm sq and 6/1/3.35 | 1.5638 | 0.2
|  |  |  | 6 | 11 KV Singadhar | 6/1/2.59 mm sq and 6/1/3.36 | 1.5638 | 0.2
47 | 33/11KV ,1x1.6 MVA Sub Station Chaned | 1.6 | 1.152 | 1 | 11 kV Local Chaned | 61/3.35, 6/1/2.59 | 1.5638 | 0.288
|  |  |  | 2 | 11 kV Parihar | 61/3.35, 6/1/2.59 | 1.5638 | 0.288
|  |  |  | 3 | 11 kV Udaipur | 61/3.35, 6/1/2.59 | 1.5638 | 0.288
|  |  |  | 4 | 11 kV Kiani (Idle) | 61/3.35, 6/1/2.59 | 1.5638 | 0.288
48 | 33/11KV , 2x1.6 Sub-Station Khushanagari | 3.2 | 1.152 | 1 | 11 KV Khushnagri | 6/1/3.35 | 2.1536 | 0.288
|  |  |  | 2 | 11 KV Seikothi | 6/1/3.35 | 2.1536 | 0.288
|  |  |  | 3 | 11 KV Jhajhakothi | 6/1/3.35 | 2.1536 | 0.288
|  |  |  | 4 | 11 kV Devikothi(Spare) | 6/1/3.35 | 2.1536 | 0.288
49 | 33/11KV 2X3.15 MVA Sub-Station Nakror | 6.3 | 2.268 | 1 | 11 KV Bhanjraru | 6/1/3.35 | 2.1536 | 0.4536
|  |  |  | 2 | 11 KV Tissa | 6/1/3.35 | 2.1536 | 0.4536
|  |  |  | 3 | 11 KV I A Energy | 6/1/3.35 | 2.1536 | 0.4536
|  |  |  | 4 | 11 KV Tikri | 6/1/3.35 | 2.1536 | 0.4536
|  |  |  | 5 | 11 KV Chanju | 6/1/3.35 | 2.1536 | 0.4536
50 | 33/11KV,2x10+1x2.5 MVA Sub-Station Chamba | 22.5 | 9.48 | 1 | 11 KV City-1 Feeder | 6/1/3.35 | 2.1536 | 0.86182
|  |  |  | 2 | 11 KV City-II Feeder | 6/1/3.35 | 2.1536 | 0.86182
|  |  |  | 3 | 11 KV Rajnoun Feeder | 6/1/3.35 | 2.1536 | 0.86182
|  |  |  | 4 | 11 KV Rajera Feeder | 6/1/3.35 | 2.1536 | 0.86182
|  |  |  | 5 | 11KV Ramgarh Feeder | 6/1/3.35 | 2.1536 | 0.86182
|  |  |  | 6 | 11 KV Pucca Tala Feeder | 6/1/3.35 | 2.1536 | 0.86182
|  |  |  | 7 | 11 KV Sarol Feeder | 6/1/3.35 | 2.1536 | 0.86182
|  |  |  | 8 | 11KV Khajjiar Feeder | 6/1/3.35 | 2.1536 | 0.86182
|  |  |  | 9 | 11 KV Kiyani Feeder | 6/1/3.35 | 2.1536 | 0.86182
|  |  |  | 10 | 11 kV Hardaspur Feeder | 6/1/3.35 | 2.1536 | 0.86182
|  |  |  | 11 | 11 KV Sahoo Feeder | 6/1/3.35 | 2.1536 | 0.86182
51 | 33/11KV ,2x3.15 Sub-Station Jarangla | 6.3 | 3 | 1 | 11 KV Rakh feeder | 6/1/3.35 | 2.1536 | 0.75
|  |  |  | 2 | 11 KV Karian Exp. Feeder | 6/1/3.35 , 6/1/2.59 | 1.5638 | 0.75
|  |  |  | 3 | 11 KV GIS-2 | XLPE Cable 3 Core 300 MM | 5.1852 | 0.75
|  |  |  | 4 | 11 KV Power Grid | XLPE Cable 3 Core 300 MM , 7/4.26 | 3.1413 | 0.75
52 | 33/11KV ,2X1.6 MVA Sub-Station Maredi | 3.2 | 2 | 1 | 11 kV Local Barour | 6/1/3.35, 6/1/2.59 | 1.5638 | 0.5
|  |  |  | 2 | 11 kV Jumhar | 6/1/3.35, 6/1/2.59 | 1.5638 | 0.5
|  |  |  | 3 | 11 KV Sahoo Feeder (New) | 6/1/3.35, 6/1/2.59 | 1.5638 | 0.5
|  |  |  | 4 | 11 kV Sungal | 6/1/3.35 | 2.1536 | 0.5
53 | 33/11KV, 2X1.6 Sub-Station Dharwala | 3.2 | 2.304 | 1 | 11 kv Gehra | 6/1/3.35, 6/1/2.59 | 1.5638 | 0.384
|  |  |  | 2 | 11 kv Radi | 6/1/3.35, 6/1/2.59 | 1.5638 | 0.384
|  |  |  | 3 | 11kv Lylh | 6/1/3.35, 6/1/2.59 | 1.5638 | 0.384
|  |  |  | 4 | 11 kv Sunara | 6/1/3.35, 6/1/2.59 | 1.5638 | 0.384
|  |  |  | 5 | 11kv NHPC | 6/1/3.35, 6/1/2.59 | 1.5638 | 0.384
|  |  |  | 6 | 11 kv Dharwala | 6/1/3.35, 6/1/2.59 | 1.5638 | 0.384
54 | 33/11 kV Sub-Station Holi | 4.75 | 0 | 1 | 11 KV Holi | 6/1/3.35 (Rabbit) | 2.1536 | 0
|  |  |  | 2 | 11 KV Nayagram | 6/1/3.35 (Rabbit) | 2.1536 | 0
|  |  |  | 3 | 11 KV Holi-Garola | 6/1/3.35 (Rabbit) | 2.1536 | 0
55 | 33/11KV, 1x1.6+1x3.15 Sub-Station Garola | 4.75 | 1.799 | 1 | 11 KV Gehra Feeder | 6/1/3.35 (Rabbit) | 2.1536 | 0.59967
|  |  |  | 2 | 11 KV Lahal | 6/1/3.35 (Rabbit) | 2.1536 | 0.59967
|  |  |  | 3 | 11 KV Garola-Holi | 6/1/3.35 (Rabbit) | 2.1536 | 0.59967
56 | 33/11KV, 2x1.6 Sub-Station Dinka( Bharmour) | 3.2 | 1.6128 | 1 | 11 KV Bharmour | 6/1/3.35 (Rabbit) | 2.1536 | 0.32256
|  |  |  | 2 | 11 KV Kugati | 6/1/3.35 (Rabbit) | 2.1536 | 0.32256
|  |  |  | 3 | 11 KV Badgram | 6/1/3.35 (Rabbit) | 2.1536 | 0.32256
|  |  |  | 4 | 11 KV Lahal | 6/1/3.35 (Rabbit) | 2.1536 | 0.32256
|  |  |  | 5 | 11 KV Budhil | 6/1/3.35 (Rabbit) | 2.1536 | 0.32256
57 | 33/11 KV Sub-Station Jassure | 20 | 8 | 1 | 11 KV Kotla | AAAC- 7/3.15, ACSR-6/1/2.59, 6/1/3.35 | 1.5638 | 1
|  |  |  | 2 | 11 KV Jassure | AAAC-7/3.15, ACSR 6/1/3.35,6/1/2.59 | 1.5638 | 1
|  |  |  | 3 | 11 KV Suliali | AAAC- 7/3.15, ACSR-6/1/2.59, 6/1/3.35 | 1.5638 | 0.5
|  |  |  | 4 | 11 KV Agro | AAAC- 7/3.15, ACSR-6/1/2.59, 6/1/3.35 | 1.5638 | 1.5
|  |  |  | 5 | 11 KV Gangath | AAAC- 7/3.15, ACSR-6/1/2.59, 6/1/3.35 | 1.5638 | 1
|  |  |  | 6 | 11 KV Nurpur | AAAC- 7/3.15, ACSR-6/1/2.59, 6/1/3.35 | 1.5638 | 1
|  |  |  | 7 | 11 KV Aund | AAAC- 7/3.15, ACSR-6/1/2.59, 6/1/3.35 | 1.5638 | 1
|  |  |  | 8 | 11 KV Colony | ACSR-6/1/2.59 | 1.5638 | 1
58 | 33/11 KV ,2X3.15 MVA Sadwan | 6.3 | 2.5 | 1 | 11 KV Niar | ACSR 6/1/2.59, AAAC 7/3.15mm | 1.5638 | 0.5
|  |  |  | 2 | 11 KV Ladori | ACSR 6/1/2.59, AAAC 7/3.15mm | 1.5638 | 0.5
|  |  |  | 3 | 11 KV Suliali-2 | ACSR 6/1/2.59, AAAC 7/3.15mm | 1.5638 | 0.5
|  |  |  | 4 | 11 KV Sadwan | ACSR 6/1/2.59, AAAC 7/3.15mm | 1.5638 | 0.5
|  |  |  | 5 | 11 KV Jal Jeewan (WSS Suliali) | ACSR 6/1/3.35mm | 2.1536 | 0.5
59 | 33/11 kV,2x3.15 MVA Sub-Station Chowari | 6.3 | 2 | 1 | 11kv Hobar feeder | 6/1/2.59 mm sq and 6/1/3.35 | 1.5638 | 0.4
|  |  |  | 2 | 11kv Chowari feeder | 6/1/2.59 mm sq and 6/1/3.35 | 1.5638 | 0.4
|  |  |  | 3 | 11kv Malunda feeder | 6/1/2.59 mm sq and 6/1/3.35 | 1.5638 | 0.4
|  |  |  | 4 | 11kv Lahru feeder | 6/1/2.59 mm sq and 6/1/3.35 | 1.5638 | 0.4
|  |  |  | 5 | 11kv Raipur feeder | 6/1/2.59 mm sq and 6/1/3.35 | 1.5638 | 0.4
60 | 33/11 kV ,2x2.5 MVA Sub-Station Bakloh | 5 | 3 | 1 | 11 KV Nenikhad Feeder | ACSR 6/1/3.35 mm Sq, 6/1/2.59 mm Sq | 1.5638 | 0.43
|  |  |  | 2 | 11 KV Magzine Feeder | ACSR 6/1/3.35 mm Sq, 6/1/2.59 mm Sq & 7/2.50 mm sq | 1.5638 | 0.43
|  |  |  | 3 | 11 KV Kakira Feeder | ACSR 6/1/3.35 mm Sq, 6/1/2.59 mm Sq | 1.5638 | 0.43
|  |  |  | 4 | 11 KV Bakloh Feeder | ACSR 6/1/3.35 mm Sq, 6/1/2.59 mm Sq | 1.5638 | 0.43
|  |  |  | 5 | 11 KV Tunuhatti Feeder | ACSR 6/1/3.35 mm Sq, 6/1/2.59 mm Sq | 1.5638 | 0.43
|  |  |  | 6 | 11 KV Chowari Feeder | ACSR 6/1/3.35 mm Sq, 6/1/2.59 mm Sq | 1.5638 | 0.43
|  |  |  | 7 | 11 KV MES Feeder | XLPE Cable 3*95 mm sq | 2.7709 | 0.43
61 | 33/11 kV,2x3.15 MVA Sub-Station Sihunta | 6.3 | 0.4536 | 1 | 11kV Sihunta feeder | 6/1/2.59 mm sq and 6/1/3.35 | 1.5638 | 0.09072
|  |  |  | 2 | 11kV Dhulara feeder | 6/1/2.59 mm sq and 6/1/3.35 | 1.5638 | 0.09072
|  |  |  | 3 | 11kV Tundi feeder | 6/1/2.59 mm sq and 6/1/3.35 | 1.5638 | 0.09072
|  |  |  | 4 | 11kV Morthu feeder | 6/1/2.59 mm sq and 6/1/3.35 | 1.5638 | 0.09072
|  |  |  | 5 | 11kV Hatli feeder | 6/1/2.59 mm sq and 6/1/3.35 | 1.5638 | 0.09072
62 | 33/11 KV,2X6.3 MVA Raja Ka Bagh | 12.6 | 9.072 | 1 | 11 KV IND No.I | ACSR 6/1/2.59 mm | 1.5638 | 1.5638
|  |  |  | 2 | 11 KV IND No.II | ACSR 6/1/2.59 mm | 1.5638 | 1.5638
|  |  |  | 3 | 11 KV Khanni | ACSR 6/1/3.35 mm | 2.1536 | 2.154
|  |  |  | 4 | 11 KV Kutta | ACSR 6/1/2.59 mm | 1.5638 | 1.5638
|  |  |  | 5 | 11 KV Naglahar | ACSR 6/1/2.59 mm | 1.5638 | 1.0638
63 | 33/11 KV,1X3.15 Attara (Gangath) | 3.15 | 1.6 | 1 | 11 KV Gangath | ACSR-6/1/3.35MM | 2.1536 | 0.4
|  |  |  | 2 | 11 KV Rit | ACSR-6/1/3.35MM | 2.1536 | 0.4
|  |  |  | 3 | 11 KV Bassa | ACSR-6/1/3.35MM | 2.1536 | 0.4
|  |  |  | 4 | 11 KV Kothi | ACSR-6/1/3.35MM | 2.1536 | 0.4
64 | 33/11 KV ,2X3.15 MVA Kotla | 6.3 | 0 | 1 | Kotla | ACSR 6/1/3.35 & 6/1/2.59 | 1.5638 | 0
|  |  |  | 2 | Soldha | ACSR 6/1/3.35 & 6/1/2.59 | 1.5638 | 0
|  |  |  | 3 | Bhalli | ACSR 6/1/3.35 & 6/1/2.59 | 1.5638 | 0
|  |  |  | 4 | Mastgarh | ACSR 6/1/3.35 & 6/1/2.59 | 1.5638 | 0
|  |  |  | 5 | Bagga | ACSR 6/1/3.35 & 6/1/2.59 | 1.5638 | 0
|  |  |  | 6 | WSS Bagga | ACSR 6/1/3.35 & 6/1/2.59 | 1.5638 | 0
65 | 33/11 KV ,1x6.3+1x3.15 MVA Thapkour | 9.45 | 6.804 | 1 | 11 KV Air Force 2nd | ACSR-6/1/3.35MM | 2.1536 | 2.1536
|  |  |  | 2 | 11 KV Dhangu Peer | ACSR-6/1/3.35MM | 2.1536 | 2.1536
|  |  |  | 3 | 11 KV Lodhwan | ACSR-6/1/3.35MM & AAAC-7/3.15MM | 2.1536 | 2.1536
66 | 33/11 KV ,2X3.15 MVA Jawali | 6.3 | 1.5 | 1 | Jawali | ACSR 6/1/3.35 & 6/1/2.59 | 1.5638 | 0.75
|  |  |  | 2 | Harsar | AAAC 7/3.81, ACSR-6/1/2.59 & 6/1/3.35 mm | 1.5638 | 0
|  |  |  | 3 | Sidhatha | ACSR 6/1/3.35 & 6/12.59 | 1.5638 | 0.75
67 | 33/11KV,2x3.15 MVA Sub-Station Fatehpur | 8.15 | 0 | 1 | 11 kV Fatehpur | ACSR-6/1/2.59MM, ACSR-6/1/3.15MM | 1.5638 | 0
|  |  |  | 2 | 11 kV Dhameta | ACSR-6/1/2.59MM, ACSR-6/1/3.15MM | 1.5638 | 0
|  |  |  | 3 | 11 kV Barot | ACSR-6/1/2.59MM, ACSR-6/1/3.15MM | 1.5638 | 0
|  |  |  | 4 | 11 kV Sihal | ACSR-6/1/2.59MM, ACSR-6/1/3.15MM | 1.5638 | 0
[5 empty] | 11kV Houri Devi feeder | ACSR 6/1/2.59 sqmm | 1.564 | 0
|  |  |  | 5 | 11 kV Palli | ACSR-6/1/2.59MM, ACSR-6/1/3.15MM | 1.5638 | 0
68 | 33/11 KV,2X5 MVA Bharmar | 10 | 6 | 1 | Jawali-I | ACSR 6/1/3.35 & 6/1/2.59 | 1.5638 | 1.2
|  |  |  | 2 | Jawali-II | ACSR 6/1/3.35 & 6/1/2.59 | 1.5638 | 1.2
|  |  |  | 3 | Fatehpur/Sidhatha | ACSR 6/1/3.35 & 6/1/2.59 | 1.5638 | 1.2
|  |  |  | 4 | Rehan-I | ACSR 6/1/3.35 & 6/1/2.59 | 1.5638 | 1.2
|  |  |  | 5 | Rehan-II | ACSR 6/1/3.35 & 6/1/2.59 | 1.5638 | 1.2
69 | 33/11KV,2x3.15 MVA Sub-Station Rehan | 6.3 | 1 | 1 | 11 KV Rehan | ACSR 6/1/3.35mm2, 6/1/2.11 mm2, 7/3.15 mm2 | 1.2209 | 0.25
|  |  |  | 2 | 11 KV Raja ka Talab | ACSR 6/1/3.35mm2, 6/1/2.11 mm2, 7/3.15 mm2 | 1.2209 | 0.25
|  |  |  | 3 | 11 KV Golwan | ACSR 6/1/3.35mm2, 6/1/2.11 mm2, 7/3.15 mm2 | 1.2209 | 0.25
|  |  |  | 4 | 11 KV Chatter | ACSR 6/1/3.35mm2, 6/1/2.11 mm2, 7/3.15 mm2 | 1.2209 | 0
|  |  |  | 5 | 11 KV Dini | ACSR 6/1/3.35mm2, 6/1/2.11 mm2, 7/3.15 mm2 | 1.2209 | 0.25
70 | 33/11KV,2X6.3 MVA MVA Sub-Station Badukhar | 12.6 | 0 | 1 | 11KV REY | ACSR 6/1/3.35MM | 2.1536 | 0
|  |  |  | 2 | 11KV BADUKHAR | ACSR 6/1/3.35MM | 2.1536 | 0
|  |  |  | 3 | 11KV BELA LUDHIYARCHAN | ACSR 6/1/3.35MM | 2.1536 | 0
|  |  |  | 4 | 11KV BHOGARWAN | ACSR 6/1/3.35MM | 2.1536 | 0
|  |  |  | 5 | 11KV SATHANA | ACSR 6/1/3.35MM | 2.1536 | 0
71 | 33/11 KV Sub Station Kandrori | 12.6 | 6 | 1 | Indora | ACSR-6/1/3.35MM & ACSR-6/1/4.09mm | 2.1536 | 0.666
|  |  |  | 2 | Rey | ACSR-6/1/3.35MM & ACSR-7/3.15mm | 2.1536 | 0.666
|  |  |  | 3 | Kandrori | ACSR-6/1/3.35MM | 2.1536 | 0.666
|  |  |  | 4 | Damtal | ACSR-6/1/3.35MM | 2.1536 | 0.666
|  |  |  | 5 | Surajpur | ACSR-6/1/3.35MM | 2.1536 | 0.666
|  |  |  | 6 | Bain 1 | ACSR-6/1/3.35MM | 2.1536 | 0.666
|  |  |  | 7 | Bain 2 | ACSR-6/1/3.35MM | 2.1536 | 0.666
|  |  |  | 8 | Agro | ACSR-6/1/3.35MM | 2.1536 | 0.666
|  |  |  | 9 | Dah | ACSR-6/1/3.35MM | 2.1536 | 0.666
72 | 33/11 KV,1x4+1X5 MVA Surajpur | 9 | 4.584 | 1 | 11 KV Surajpur NO-I | ACSR-6/1/2.11MM & 6/1/3.35MM | 1.2209 | 0.9168
|  |  |  | 2 | 11 KV Surajpur No-II | ACSR-6/1/2.11MM | 1.2209 | 0.9168
|  |  |  | 3 | 11 KV Airforce | ACSR-6/1/3.35MM | 2.1536 | 0.9168
|  |  |  | 4 | 11 KV Gangath | ACSR-6/1/3.35MM | 2.1536 | 0.9168
|  |  |  | 5 | 11 KV Dah | ACSR-6/1/3.35MM | 2.1536 | 0.9168
73 | 33/11 KV,2X6.3 MVA Damtal (Unmanned) | 12.6 | 6 | 1 | 11 KV Surajpur 1st | ACSR-6/1/3.35MM | 2.1536 | 2
|  |  |  | 2 | 11 KV Mh- Mazra | ACSR-6/1/2.11MM | 1.2209 | 2
|  |  |  | 3 | 11 KV Surajpur 2nd | ACSR-6/1/3.35MM | 2.1536 | 2
74 | 33/11 KV ,2X10/12.5 MVA Malot | 25 | 5 | 1 | 11 KV Outgoing-7 | ACSR-6/1/3.35MM | 2.1536 | 1.25
|  |  |  | 2 | 11 KV Outgoing-8 | ACSR-6/1/3.35MM | 2.1536 | 1.25
|  |  |  | 3 | 11 KV Outgoing-9 | ACSR-6/1/3.35MM | 2.1536 | 1.25
|  |  |  | 4 | 11 KV Outgoing-5 | ACSR-6/1/3.35MM | 2.1536 | 1.25
75 | 33/11KV,2X6.3 MVA Sub-Station Thakurdwara | 12.6 | 7 | 1 | 11 KV Barota | ACSR-6/1/3.35MM | 2.1536 | 1.4
|  |  |  | 2 | 11 KV Paral | ACSR-6/1/3.35MM | 2.1536 | 1.4
|  |  |  | 3 | 11 KV Thakurdwara | ACSR-6/1/3.35MM | 2.1536 | 1.4
|  |  |  | 4 | 11 KV Shahanehar | ACSR-6/1/2.59MM & 6/1/3.35MM | 1.5638 | 1.4
|  |  |  | 5 | 11 KV Mand Miani | ACSR-7/3.81MM | 2.7298 | 1.4
76 | 33/11 kV Sub-Station Bharoli Jadid | 3.15 | 0 | 1 | 11kV Rakkar | ACSR 6/1/2.11 & AAAC 7/3.15mm² | 1.221 | 0
|  |  |  | 2 | 11kV Sard Dogri | ACSR 6/1/2.59mm² | 1.5638 | 0
|  |  |  | 3 | 11kV Pirsaluhi | ACSR 6/1/2.11 & AAAC 7/3.15mm² | 1.221 | 0
|  |  |  | 4 | 11kV Kamloo | AAAC 7/3.15mm² | 2.1674 | 0
77 | 33/11 kV Jawalamukhi | 6.3 | 1 | 1 | 11 kV Chambapattan Feeder | AAAC 7/3.81 mm2 | 2.7298 | 0
|  |  |  | 2 | 11 kV Kohala Feeder | AAAC 7/4.26 mm2 | 3.1413 | 0.2
|  |  |  | 3 | 11 Kv Surani Feeder | AAAC 7/3.81 mm2 | 2.7298 | 0.2
|  |  |  | 4 | 11 KV No1 Jawalamukhi Feeder | AAAC 7/4.26 mm2 | 3.1413 | 0.2
|  |  |  | 5 | 11 kV No 2 Jawalamukhi Feeder | AAAC 7/3.81 mm2 | 2.7298 | 0.2
|  |  |  | 6 | 11 kV Khundian Feeder | AAAC 7/3.81 mm2 | 2.7298 | 0.2
78 | 33/11 kV 2*1.6 MVA Substation Khundian | 3.2 | 0.5 | 1 | 11Kv Thill Feeder | 7/4.26AAAC | 3.1413 | 0.1
|  |  |  | 2 | 11Kv Dolla Feeder | 6/1/3.35 | 2.1536 | 0.1
|  |  |  | 3 | 11Kv Nahalian Feeder | 7/4.26AAAC | 3.1413 | 0.1
|  |  |  | 4 | 11Kv Saprallu Feeder | 6/1/3.35 | 2.1536 | 0.1
|  |  |  | 5 | 11Kv Bhim Godda Feeder | 7/4.26AAAC | 3.1413 | 0.1
79 | 33/11 kV Kohla | 4.75 | 1.752 | 1 | 11 kV Kohla Malankar | AAAC 7/4.26sqmm | 3.1413 | 0.876
|  |  |  | 2 | 11 kV Nadaun IPH Feeder | AAAC 7/4.26sqm, 7/3.81 sq m | 2.7298 | 0.876
| Total | 625.5 | 216.3617 |  |  |  |  | 216.6623

## Hamirpur Zone
Notification of sub-station & Feeder wise surplus capacity which can be fed from RE Power Plants under Hamirpur Zone.
Sr. No. | Name of Sub-Station | Transformation capacity Installed at 33/11 kV Level (MVA) | Surplus Transformation capacity available at 132/11kV, 33/11 kV & 33/22 kV Level (MW) |  |  |  |  | Remarks
|  |  |  | Name of Feeder | Type of Conductor | Maximum Capacity of Feeder as per type of Conductor (in MW) | Min Rational Capacity of Feeder as per Surplus Transformation Capacity (Without Minimum Loading of Feeder) (in MW)
1 | 33/11 kV sub-station Jabli | 12.6 | 4.143 | 11 KV Jabli – Bilaspur No.I | AAAC 7/4.26mm | 3.1413 | 0.69
|  |  |  | 11 KV Jabli – Bilaspur No.II | AAAC 7/4.26mm | 3.1413 | 0.69
|  |  |  | 11 KV Jabli – Bilaspur No.III | AAAC 7/4.26mm | 3.1413 | 0.69
|  |  |  | 11 KV Jabli - Rishikesh | AAAC 7/4.26mm | 3.1413 | 0.69
|  |  |  | 11 KV Jabli - Kothipura | AAAC 7/4.26mm | 3.1413 | 0.69
|  |  |  | 11 KV Jabli - Chharol | AAAC 7/4.26mm | 3.1413 | 0.69
2 | 33/11kV Namhol | 5 | 1.16 | 11 KV Namhol – Namhol | ACSR 6/1/3.35mm and 6/1/2.59mm | 1.5638 | 0.29
|  |  |  | 11 KV Namhol – Chhakoh | AAAC 7/4.26mm, ACSR 6/1/2.59MM | 1.5638 | 0.29
|  |  |  | 11 KV Namhol – Jukhala | ACSR 6/1/3.35mm, and 6/1/2.59mm | 1.5638 | 0.29
|  |  |  | 11 KV Namhol - Brahampukhar | ACSR 6/1/3.35mm | 2.1536 | 0.29
3 | 33/11kV Beri | 6.3 | 1.322 | 11 KV Beri – Barmana | AAAC 7/4.26mm, ACSR 6/1/2.59MM | 1.5638 | 0.335
|  |  |  | 11 KV Beri – Panjgain | AAAC 7/4.26mm | 3.1413 | 0.335
|  |  |  | 11 KV Beri – Beri | ACSR 6/1/2.59MM | 1.5638 | 0.335
|  |  |  | 11 KV Beri - Ghagus | AAAC 7/4.26mm | 3.1413 | 0.335
4 | 33/11kV Jukhala | 6.3 | 2.22 | 11 KV Rani Kolta | ACSR 6/1/3.35mm and 6/1/2.59mm | 1.5638 | 0.37
|  |  |  | 11 KV Bathoh | ACSR 6/1/2.59MM | 1.5638 | 0.37
|  |  |  | 11 KV Dadhog | ACSR 6/1/3.35mm and 6/1/2.59mm | 1.5638 | 0.37
|  |  |  | 11 KV LWSS AIIMS | ACSR 6/1/4.72mm | 3.2785 | 0.37
|  |  |  | 11kV Kolanu feeder | ACSR 6/1/3.35mm | 2.154 | 0.37
|  |  |  | 11 KV Bandla | ACSR 6/1/4.72mm and ACSR 6/1/2.59mm | 1.5638 | 0.37
5 | 33/11kV,1x6.30 MVA Sub-Station Swarghat | 12.6 | 1 | 11 KV Swarghat - Zakatkhana | ACSR 6/1/3.35mm and 6/1/2.59mm | 1.5638 | 0.25
|  |  |  | 11 KV Swarghat - Swahan | ACSR 6/1/3.35mm and 6/1/2.59mm | 1.5638 | 0.25
|  |  |  | 11 KV Swarghat - New Local | ACSR 6/1/3.35mm and 6/1/2.59mm | 1.5638 | 0.25
|  |  |  | 11KV Nand V.C.B. | ACSR 6/1/3.35mm and 6/1/2.59mm | 1.5638 | 0.25
6 | 33/11 kV sub-station Kot | 4.15 | 1 | 11 KV Kot – Sri Naina Devi Ji | ACSR 6/1/3.35mm and 6/1/2.59mm | 1.5638 | 0.25 | Berra Dol SPP 5 MW at 33kV level.
|  |  |  | 11 KV Kot – LWSS-I Sri Naina Devi Ji | ACSR 6/1/3.35mm | 2.1536 | 0.25
|  |  |  | 11 KV Kot – LWSS-II Sri Naina Devi Ji | ACSR 6/1/3.35mm and 7/3.15mm | 2.1536 | 0.25
|  |  |  | 11 KV Kot – Bassi | ACSR 6/1/3.35mm and 6/1/2.59mm | 1.5638 | 0.25
7 | 33/11kV Gamber | 3.15 | 1.3608 |  |  |  | 0
8 | 33/11kV Dabat | 6.3 | 2.7216 |  |  |  | 0
9 | 33/11 kV Sub-Station. Kandrour | 12.6 | 3.2 | 11 kv Geharwin Feeder | ACSR 6/1/4.72 mm 6/1/4.09 mm,6/1/3.35mm,6/1/2.59mm, 6/1/2.11mm | 1.2209 | 0.4
|  |  |  | 11 kv Talyana Feeder | ACSR 6/1/4.09 mm,6/1/3.35mm,6/1/2.59mm, 6/1/2.11mm | 1.2209 | 0.4
|  |  |  | 11 kv Delag Feeder | ACSR 6/1/4.09 mm,6/1/3.35mm,6/1/2.59mm, 6/1/2.11mm | 1.2209 | 0.4
|  |  |  | 11 kv Kothi Chand pur | ACSR 6/1/4.09 mm,6/1/3.35mm,6/1/2.59mm, 6/1/2.11mm | 1.2209 | 0.4
|  |  |  | 11 Kv I&PH Biyater | ACSR 6/1/4.09 mm,6/1/3.35mm,6/1/2.59mm, 6/1/2.11mm | 1.2209 | 0.4
|  |  |  | 11 kv Ghumarwin Feeder | ACSR 6/1/4.09 mm,6/1/3.35mm,6/1/2.59mm, 6/1/2.11mm | 1.2209 | 0.4
|  |  |  | 11 kv Harlog Feeder | ACSR 6/1/4.09 mm,6/1/3.35mm,6/1/2.59mm, 6/1/2.11mm | 1.2209 | 0.4
|  |  |  | 11 kv Kungar Hatti Feeder | ACSR 6/1/4.09 mm,6/1/3.35mm,6/1/2.59mm, 6/1/2.11mm | 1.2209 | 0.4
10 | 33/11kV Sub-Station. Bharari | 6.3 | 0 | 11KV Bharari-Malot-hatwar feeder | ACSR 6/1/4.72 | 3.2785 | 0 | SS Chauhan SPP 5 MW on 33kV Bharari-Jahu line. Due to this capacity is exhausted.
|  |  |  | 11KV Bharari-Marhana feeder | AAAC 7/3.81 | 2.7298 | 0
|  |  |  | 11kv Bharari-Talwara feeder | ACSR 6/1/4.72 | 3.2785 | 0
|  |  |  | 11KV Bharari-Chakrana feeder | AAAC 7/3.81 | 2.7298 | 0
|  |  |  | 11KV Bharari-Barota feeder | AAAC 7/3.81 | 2.7298 | 0
11 | 33/11 kV Naswal | 12.6 | 5.064 | 11 KV Ghumarwin 1st | AAAC,7/4.26 AAAC,7/3.15 ACSR,6/1/2.11 ACSR,6/1/3.35 H.T. AB CABLE, 3*95 sq. mm | 1.2209 | 0.46785
|  |  |  | 11 kv Dangar | AAAC,7/4.26 AAAC,7/3.15 ACSR,6/1/2.11 ACSR,6/1/2.59 | 1.2209 | 0.766
|  |  |  | 11 KV Ghumarwin 3rd | H.T. AB CABLE, 3*95 sq. mm | 3.155 | 0.766
|  |  |  | 11 KV Ghumarwin 2nd | AAAC,7/4.26 AAAC,7/3.15 ACSR,6/1/2.11 ACSR,6/1/3.35 H.T. AB CABLE, 3*95 sq. mm | 1.2209 | 0.766
|  |  |  | 11 kv Gahar Padhyan | AAAC,7/4.26 AAAC,7/3.15 ACSR,6/1/2.11 ACSR,6/1/3.35 H.T. AB CABLE, 3*95 sq. mm | 1.2209 | 0.766
|  |  |  | 11 kv Kuthera | AAAC,7/3.15 ACSR,6/1/2.11 ACSR,6/1/3.35 | 1.2209 | 0.766
|  |  |  | 11 kv Berthin | AAAC,,7/3.15 AAAC,7/3.81 ACSR,6/1/2.59 | 1.5638 | 0.766
12 | 33/11 kV Sub-Station. Jhabola | 6.3 | 2.1216 | Jhabola Talai | AAAC 7/3.15 mm2 (55 mm)& AAAC 7/3.81 mm2 (80 mm) | 2.1674 | 0.42432 | NS Solar Energy has been granted connectivity on 33kV Jhabola-Kutbanger line.
|  |  |  | Jhabola Gharan | AAAC 7/3.15 mm2 (55 mm)& ACSR 6/1/2.11 mm2 (20 mm) | 1.2209 | 0.42432
|  |  |  | Jhabola Koserian | AAAC 7/3.15 mm2 (55 mm) & ACSR 6/1/2.59 mm2 (30 mm) | 1.5638 | 0.42432
|  |  |  | Jhabola Bal-seena | AAAC 7/3.15 mm2 (55 mm)& ACSR 6/1/2.11 mm2 (20 mm) | 1.2209 | 0.42432
|  |  |  | Jhabola Talai (AB Cable) | 11 KV AB Cable 95 mm2 | 3.155 | 0.42432
13 | 33/11 kV Sub-Station. Jhandutta | 6.3 | 2.1216 | 11kv kalol | 6/1/3.75 | 2.1536 | 0.30309
|  |  |  | 11kv Nakhlera | 7/3.81 | 2.7298 | 0.30309
|  |  |  | 11kv talai | 7/3.15 | 2.1674 | 0.30309
|  |  |  | 11kv jhandutta | 6/1/2.11 | 1.2209 | 0.30309
|  |  |  | 11kv berthin | 6/1/2.11 | 1.2209 | 0.30309
|  |  |  | 11kv amroha | 6/1/2.11 | 1.2209 | 0.30309
|  |  |  | 11kv Nerus | 6/1/3.35 | 2.1536 | 0.30309
14 | 33/11 kV Berthin | 6.3 | 2.7216 | 11KV SUNHANI | AAAC 7/4.26 MM2 | 3.1413 | 0.54432
|  |  |  | 11 KV BERTHIN-LOCAL | AAAC 7/4.26 MM2 | 3.1413 | 0.54432
|  |  |  | 11 KV BALSHEENA | AAAC 7/4.26 MM2 | 3.1413 | 0.54432
|  |  |  | 11 KV CHATT KARLOTI | AAAC 7/4.26 MM2 | 3.1413 | 0.54432
|  |  |  | 11 KV KAPHARA | AAAC 7/4.26 MM2 | 3.1413 | 0.54432
15 | 33/11 kV Ram Bag | 6.3 | 4.536 | 11 KV Ram Bag Stage No -1 | ACSR 6/1/4.09 mm, | 2.7435 | 1.134
|  |  |  | 11 KV Ram Bag Stage (spare Stand By) | ACSR 6/1/4.09 mm, | 2.7435 | 1.134
|  |  |  | 11 Ram Bag Stage-2 (Beri Rajadiyan) | ACSR 6/1/4.09 mm, | 2.7435 | 1.134
|  |  |  | 12 Ram Bag Stage-2 (Beri Rajadiyan) Stand By. | ACSR 6/1/4.09 mm, | 2.7435 | 1.134
16 | 66/11kV,1x6.3 MVA Sub-Station Gowlthai | 6.3 | 4.036 | 11 kV Bhakhra Feeder | ACSR 6/1/3.35 MM2 | 2.1536 | 1.3453
|  |  |  | 11 kV Industrial Phase-II | AAAC 7/4.26 MM2 | 3.1413 | 1.3453
|  |  |  | 11 kV Bassi | ACSR 6/1/4.72 MM2 | 3.2785 | 1.3453
17 | 33/11 kV Sub-Station Mattansidh | 6.3 | 3.6324 | 11 KV Lambloo | AAAC 7/3.81mm2, ACSR 6/1/2.59mm2 | 1.5638 | 0.52
|  |  |  | 11kV Tikker | AAAC 7/3.81mm2, ACSR 6/1/2.59mm2 | 1.5638 | 0.52
|  |  |  | 11 KV Tappan Pet | HT AB Cable 3x120mm | 3.5665 | 0.52
|  |  |  | 11kV Mattan Hamirpur | AAAC 7/3.81mm2 | 2.7298 | 0.52
|  |  |  | 11kV Industrial | AAAC 7/3.81mm2 | 2.7298 | 0.52
18 | 33/11 kV Sub- Station Gasota | 6.3 | 4.0824 | 11 KV BOHNI | AAAC 7/4.26mm2 | 3.1413 | 0.6804
|  |  |  | 11 KV THANA | AAAC 7/4.26mm2 | 3.1413 | 0.6804
|  |  |  | 11 KV TAL | AAAC 7/4.26mm2 | 3.1413 | 0.6804
|  |  |  | 11 KV LAMBLOO | AAAC 7/4.26mm2 | 3.1413 | 0.6804
|  |  |  | 11 KV BALOO | AAAC 7/4.26mm2 | 3.1413 | 0.6804
|  |  |  | SPARE | AAAC 7/4.26mm2 | 3.1413 | 0.6804
19 | 33/11 kV Sub-Station Bhota | 2.6 | 1.6848 | 11 kV RSSB Bhota-1 | AAAC7/3.81 mm | 2.7298 | 0.8424
|  |  |  | 11 kV RSSB Bhota -II | AAAC7/3.81 mm | 2.7298 | 0.8424
20 | 33/11 kV Sub-Station Kotla (Bijhar) | 6.3 | 2.6 | 11 kV Bijhar | AAAC 7/3.15 mm, AAAC 7/3.81 mm, ACSR 6/1/3.35 mm | 2.1536 | 0.65468
|  |  |  | 11 kV Bijhar - Dhangota | AAAC 7/3.15 mm, AAAC 7/3.81 mm, ACSR 6/1/3.35 mm & ACSR 6/1/2.59 mm | 1.5638 | 0
|  |  |  | 11 kV Bijhar - Maharal | AAAC 7/3.15 mm, AAAC 7/3.81 mm & ACSR 6/1/3.35 mm | 2.1536 | 0.65468
|  |  |  | 11 kV Bijhar - X-Press Maharal | AAAC 7/3.15 mm, AAAC 7/3.81 mm & ACSR 6/1/3.35 mm | 2.1536 | 0.65468
|  |  |  | 11 kV Bijhar- Chakmoh | AAAC 7/3.15 mm, AAAC 7/3.81 mm & ACSR 6/1/3.35 mm | 2.1536 | 0.65468
21 | 33/11 kV Sub-Station Barsar | 6.3 | 3.8574 | 11 kV Barsar | AAAC 73.81 mm & ACSR 6/1/3.35 mm | 2.1536 | 0.55106
|  |  |  | 11 kV Barsar - Harsour | AAAC 7/3.81 mm & ACSR 6/1/3.35 mm | 2.1536 | 0.55106
|  |  |  | 11 kV Barsar -Dandroo | ACSR 6/1/2.59 mm & ACSR 6/1/3.35 mm | 1.5638 | 0.55106
|  |  |  | 11 kV Barsar - Garli | AAAC 7/3.15 mm, AAAC 7/3.81 mm & AAAC 7/2.54 mm | 1.989 | 0.55106
|  |  |  | 11 kV Barsar - Salouni | ACSR 6/1/2.59 mm, AAAC 7/3.81 mm & ACSR 6/1/3.35 mm | 1.5638 | 0.55106
|  |  |  | 11 kV Barsar - Khawaja | AAAC 7/3.81 mm &ACSR 6/1/3.35 mm | 2.1536 | 0.55106
|  |  |  | 11 kV Barsar- Steel Industry | AAAC 7/3.81 | 2.73 | 0.55106
22 | 33/11 kV Sub-Station Ukhali | 6.3 | 4.0824 |  |  | 0 | 0
23 | 33/11 kV Galore | 6.3 | 4.536 | 11KV Galore | 7/3/81 AAAC | 2.7298 | 0.9072
|  |  |  | 11KV Dhaned | 7/3/81 AAAC | 2.7298 | 0.9072
|  |  |  | 11KV Kangoo | 7/3/81 AAAC | 2.7298 | 0.9072
|  |  |  | 11KV Phahal | 7/3/81 AAAC | 2.7298 | 0.9072
|  |  |  | 11KV Hareta | 7/3/81 AAAC | 2.7298 | 0.9072
24 | 33/11 kV Sub- Station Khaggal | 6.3 | 4.2 | 11 KV Jhaniari | AAAC 7/4.26mm2 | 3.1413 | 0.7
|  |  |  | 11 KV Nalti | AAAC 7/4.26mm2 | 3.1413 | 0.7
|  |  |  | 11 KV Ropa | AAAC 7/4.26mm2 | 3.1413 | 0.7
|  |  |  | 11 KV Masyana | AAAC 7/4.26mm2 | 3.1413 | 0.7
|  |  |  | 11kV Daruhi | AAAC 7/3.81mm2 | 2.73 | 0.7
|  |  |  | 11 KV Neri | AAAC 7/4.26mm2 | 3.1413 | 0.7
25 | 33/11 kV Sub- Station Tauni Devi | 8.5 | 3.102 | 11 KV Tauni Devi Local (Naughin) | AAAC 7/3.81mm2, AAAC 7/3.15mm2,ACSR 6/1/2.11mm2 | 1.2209 | 0.15
|  |  |  | 11 KV Touni devi-Kot | AAAC 7/3.81mm2, AAAC 7/3.15mm2,ACSR 6/1/2.11mm2 | 1.2209 | 0.15
|  |  |  | 11 KV Touni devi-Barin Mandir | AAAC 7/3.81mm2, AAAC 7/3.15mm2,ACSR 6/1/2.11mm2 | 1.2209 | 0.15
|  |  |  | 11 KV Touni devi-Tikkeri | AAAC 7/3.81mm2, AAAC 7/3.15mm2,ACSR 6/1/2.11mm2 | 1.2209 | 0.15
|  |  |  | 11 KV Touni devi-Uhal | AAAC 7/3.81mm2, AAAC 7/3.15mm2 | 2.1674 | 0.15
|  |  |  | 11 KV Touni devi- Matlana -I | ACSR 6/1/4.72mm2 | 3.2785 | 0.15
|  |  |  | 11 KV Touni devi- Matlana -II | ACSR 6/1/4.72mm2 | 3.2785 | 0.15
26 | 33/11 kV Sub- Station Chabutra | 3.2 | 1.6128 | 11 KV Longni feeder | AAAC 7/3.15 mm | 2.1674 | 0.8064
|  |  |  | 11 KV Barbdar feeder | AAAC 7/3.15 mm | 2.1674 | 0.8064
27 | 33/11 kV Sub- Station Patlander (Ansla) | 6.3 | 3.1752 |  |  | 0 | 0
28 | 33/11 kV Sub- Station Sujanpur | 7 | 3.528 | 11 KV Sujanpur | AAAC 7/4.26 mm | 3.1413 | 0.7056
|  |  |  | 11 KV Tihra | AAAC 7/4.26 mm | 3.1413 | 0.7056
|  |  |  | 11 KV Chabutra | AAAC 7/3.81 mm | 2.7298 | 0.7056
|  |  |  | 11 KV Patlander | AAAC 7/3.81 mm | 2.7298 | 0.7056
|  |  |  | 11 KV Jangal Beri | AAAC 7/4.26 mm | 3.1413 | 0.7056
29 | 33/11 kV Rangas | 4.2 | 3.024 | 11 kV Jolsappar | AAAC 7/4.26sqm | 3.1413 | 0.6048
|  |  |  | 11kV Balduhak | AAAC 7/4.26sqm | 3.1413 | 0.6048
|  |  |  | 11kV Rail Dangari | AAAC 7/4.26sqm | 3.1413 | 0.6048
|  |  |  | 11kV Kangoo | AAAC 7/4.26sqm | 3.1413 | 0.6048
|  |  |  | 11kV Nounghi | AAAC 7/4.26sqm | 3.1413 | 0.6048
30 | 33/11 kV Dhaneta | 4.75 | 1.23 | Dhaneta-Badaran | 7/3/81 AAAC | 2.7298 | 0.41
|  |  |  | Dhaneta-Pansai | 7/3/81 AAAC | 2.7298 | 0.41
|  |  |  | Dhaneta-Kashmir | 7/3/81 AAAC | 2.7298 | 0.41
31 | 33/11 kV Sub- Station Kakkar | 6.3 | 4.536 | 11kV Uhal | AAAC 7/3.81 mm | 2.7298 | 0.756
|  |  |  | 11 KV Kakkar | AAAC 7/3.81 mm | 2.7298 | 0.756
|  |  |  | 11 KV Bajrol | AAAC 7/3.81 mm | 2.7298 | 0.756
|  |  |  | 11 KV Bouroo-1 | AAAC 7/3.81 mm | 2.7298 | 0.756
|  |  |  | 11 KV Bouroo-II | AAAC 7/3.81 mm | 2.7298 | 0.756
|  |  |  | 11 KV Bouroo-III (Stand by) | AAAC 7/3.81 mm | 2.7298 | 0.756
32 | 33/11 kV Sub- Station Jakhu | 6.3 | 4.536 | 11 KV LWSS Mewa Bamson | AAAC 7/4.26 mm | 3.1413 | 1.134
|  |  |  | 11 KV LWSS Lagwalti Bamson | AAAC 7/4.26 mm | 3.1413 | 1.134
|  |  |  | 11 KV LWSS Bhoranj | AAAC 7/4.26 mm | 3.1413 | 1.134
|  |  |  | 11 KV Kheri | AAAC 7/4.26 mm | 3.1413 | 1.134
33 | 33/11 kV Sub- Station LWSS Palahi | 6.3 | 4.536 | 11 KV LWSS Hamirpur Town | AAAC 7/4.26 mm | 3.1413 | 1.512
|  |  |  | 11 KV LWSS Lambloo | AAAC 7/4.26 mm | 3.1413 | 1.512
|  |  |  | 11 KV LWSS Patlander | AAAC 7/4.26 mm | 3.1413 | 1.512
34 | 132/33/11 kV Nadaun (Gaggal) | 12.6 | 0 | 11 kV Bhumpal | AAAC 7/4.26sqm, 7/3.81 sq m | 2.7298 | 0
|  |  |  | 11 kV Dhaneta | AAAC 7/4.26sqm, 7/3.81 sq m | 2.7298 | 0
|  |  |  | 11 kV Silh | AAAC 7/4.26sqm, 7/3.81 sq m | 2.7298 | 0
|  |  |  | 11 kV Majheen | AAAC 7/4.26sqm, 7/3.81 sq m | 2.7298 | 0
|  |  |  | 11 kV Bara | AAAC 7/4.26sqm, 7/3.81 sq m | 2.7298 | 0
|  |  |  | 11 kV Amtar Bharoli | AAAC 7/4.26sqm, 7/3.81 sq m | 2.7298 | 0
|  |  |  | 11 kV Nadaun | AAAC 7/4.26sqm, 7/3.81 sq m | 2.7298 | 0
|  |  |  | 11 kV Kohla Sera | AAAC 7/4.26sqm, 7/3.81 sq m | 2.7298 | 0
35 | 33/11 kV Tillu | 12.6 | 5.4432 | 11 kV IPH Feeder | AAAC 7/3.81 sq m | 2.7298 | 2.7298
36 | 33/11 kV Pattaji | 6.3 | 2.7216 | 11kV SJVNL | AAAC 7/4.26sqmm | 3.1413 | 0.6804
|  |  |  | 11kV Pattaji | AAAC 7/4.26sqmm | 3.1413 | 0.6804
|  |  |  | 11klV Bara | AAAC 7/4.26sqm, 7/3.81 sq m | 2.7298 | 0.6804
|  |  |  | 11kV Choa Chakrala | AAAC 7/4.26sqmm | 3.1413 | 0.6804
37 | 33/11 kV Ladrour | 7.5 | 0 | 11 kV Ladrour -Bhota | AAAC 7/3.81 mm, ACSR 6/1/3.35 mm | 2.1536 | 0
|  |  |  | 11 kV Ladrour -Mair | AAAC 7/3.81mm, ACSR 6/1/3.35 mm & ACSR 6/1/2.59 mm | 1.5638 | 0
|  |  |  | 11 kV Ladrour -Kharwar | AAAC 7/4.26 mm, ACSR 6/1/3.35 mm & ACSR 6/1/2.59 mm | 1.5638 | 0
|  |  |  | 11 kV Ladrour - Jahu | AAAC 7/3.81 mm & ACSR 6/1/2.59 mm | 1.5638 | 0
|  |  |  | 11 kV Ladrour - Jakhyol | AAAC 7/4.26 mm & ACSR 6/1/3.35 mm | 2.1536 | 0
|  |  |  | 11 kV Ladrour -Gandalwin | AAAC 7/4.26 mm & ACSR 6/1/2.11 mm | 1.2209 | 0
38 | 33/11 kV Bhoranj | 5 | 3.6 | 11 kV Bhoranj | AAAC 7/3.15 mm & AAAC 7/3.81 mm | 2.1674 | 0.51429
|  |  |  | 11 kV Ex-Press Bhoranj | ACSR 6/1/3.35 mm & AAAC 7/3.81 mm | 2.1536 | 0.51429
|  |  |  | 11 kV Bhoranj -Deral- Parol | AAAC 7/3.15 mm, AAAC 7/2.50 mm , ACSR 6/1/3.35 mm & AAAC 7/3.81 mm | 1.6324 | 0.51429
|  |  |  | 11 kV Bhoranj -Micro-wave | ACSR 6/1/3.35 mm | 2.1536 | 0.51429
|  |  |  | 11 kV Bhoranj-Luddar | AAAC 7/3.15 mm & AAAC 7/4.26 mm | 2.1674 | 0.51429
|  |  |  | 11 kV Bhoranj - Toh | AAAC 7/3.15 mm, AAAC 7/3.81 mm, ACSR 6/1/3.35 mm | 2.1536 | 0.51429
|  |  |  | 11 kV Bhoranj -Bhareri | AAAC 7/3.15 mm & AAAC 7/3.81 mm | 2.1674 | 0.51429
39 | 33/11 kV Naltu | 6.3 | 0 | 11KV Naltu- Bhareri | AAAC 7/3.15 mm, AAAC 7/3.81 mm , AAAC 7/4.26 mm & ACSR 6/1/3.35 mm | 2.1536 | 0
|  |  |  | 11KV Naltu ludder | AAAC 7/3.15 mm, AAAC 7/3.81 mm , AAAC 7/4.26 mm & ACSR 6/1/3.35 mm | 2.1536 | 0
|  |  |  | 11KV Naltu-Jahu | AAAC 7/3.15 mm, AAAC 7/3.81 mm & ACSR 6/1/3.35 mm | 2.1536 | 0
40 | 33/11 kV Jahu | 3.2 | 0 | 11KV Jahu | AAAC 7/3.15 mm & AAAC 7/3.81 mm | 2.1674 | 0
|  |  |  | 11KV Jahu-Sulghwan | ACSR 6/1/3.35 mm | 2.1536 | 0
|  |  |  | 11KV Jahu-Manoh | ACSR 6/1/3.35 mm & AAAC 7/3.81 mm | 2.1536 | 0
41 | 132/11 kV Sub-Station Gagret | 31.5 | 0 | 11 kV Supermax | AAAC 7/4.26 mm2 | 3.9273 |  | Capacity is exhausted due to constraints at EHV level i.e. at 132kV D/C Amb-Nehrian line and 220/132kV Nehrian S/Stn.
|  |  |  | 11 kV Ind-2 | ACSR 6/1/4.72 mm2 | 4.098 | 0
|  |  |  | 11 kV Ind-1 | ACSR 6/1/4.72 mm2 | 4.098 | 0
|  |  |  | 11 kv Bharwain | ACSR 6/1/4.72 mm2 | 4.098 | 0
|  |  |  | 11 kv JME | AAAC 7/4.26 mm2 | 3.9273 | 0
|  |  |  | 11 KV Polytyech | AAAC 7/4.26 mm2 | 3.9273 | 0
42 | 33/11 kV Sub-Station Jeetpur | 8.15 | 0 | 11KV jeetpur-Gondpur Bnehra | ACSR 6/1/2.59 mm² | 1.955 | 0 | Capacity is exhausted due to constraints at EHV level i.e. at 132kV D/C Amb-Nehrian line and 220/132kV Nehrian S/Stn.
|  |  |  | 11KV Jeetpur Behri(Ind) | AAAC 7/4.26 mm² | 3.9273 | 0
|  |  |  | 11KV manika madule | AB Cable 120 mm² | 4.458 | 0
|  |  |  | 11KV Nobe Vien | AAAC 7/4.26 mm² | 3.9273 | 0
43 | 33/11 kV Sub-Station Gagret | 12.6 | 0 | 11 kv Gagret-1 | AAAC 7/4.26 mm2 | 3.9273 | 0 | Net injection exceeds existing transformation capacity.
|  |  |  | 11 kv Gagret-2 | AAAC 7/4.26 mm2 | 3.9273 | 0
|  |  |  | 11 Kv Panjawar | AAAC 7/4.26 mm2 | 3.9273 | 0
|  |  |  | 11 kv Express | AAAC 7/4.26 mm2 | 3.9273 | 0
|  |  |  | 11 kv Deoli | AAAC 7/4.26 mm2 | 3.9273 | 0
44 | 33/11 kV Sub-Station Khad | 6.3 | 0 | 11KV Khad feeder | AAAC 7/4.26 (100sq.mm) & ACSR 6/1.2.11 conductor | 1.526 | 0 | Capacity exhausted due to EHV constraints at 132/33kV Power T/Fs at 132/33kV Rakkar (Una) S/Stn, 132kV S/C Amb-Rakkar line, 132kV D/C Amb-Nehrian line and 220/132kV Nehrian S/Stn.
|  |  |  | 11KV Ispur Pandoga feeder | AAAC 7/4.26 (100sq.mm) & ACSR 6/1.2.11 conductor | 1.526 | 0
|  |  |  | 11KV Pandoga Industry feeder | AAAC 7/4.26 (100sq.mm) | 3.9273 | 0
45 | 33/11 kV Sub-Station Amb | 16.3 | 0 | 33 KV Amb - Chaksarai Feeder | AAAC 7/4.26 mm² | 11.78 | 0 | 2000 KW at 33 KV Amb- Chaksarai Feeder, M/S Surya Solar 1000 KW at 33 KV Amb - Chaksarai Feeder, Shree Sai SPP 2.5 MW at 33kV level, Arya Green Energies 4.5 MW, 3 Nos. SPPs having capacity 5 MW each (Total 15 MW). Capacity exhausted due to EHV constraints at 132/33kV Power T/Fs at 132/33kV Amb S/Stn, 132kV D/C Amb-Nehrian line and 220/132kV Nehrian S/Stn.
|  |  |  | 11KV Amb | AAAC 7/4.26 mm² | 3.9273 | 0
|  |  |  | 11 KV Dhussara | AAAC 7/4.26 mm² | 3.9273 | 0
|  |  |  | 11 KV Panjoya | AAAC 7/4.26 mm² | 3.9273 | 0
|  |  |  | 11 KV Jowar | AAAC 7/4.26 mm² | 3.9273 | 0
|  |  |  | 11 KV Sona-lika | AAAC 7/4.26 mm² | 3.9273 | 0
|  |  |  | 11 KV Sidhpur | AAAC 7/4.26 mm² | 3.9273 | 0
|  |  |  | 11 KV Koharchhan | AAAC 7/3.15 mm² | 2.7094 | 0
46 | 33/11 kV Sub-Station Daulatpur | 12.6 | 0 | 11 kv Daulatpur | AAAC 7/4.26, 7/315 mm, 6/1/2.59 mm & 2.11 mm (mixed ) | 1.562 | 0 | Capacity exhausted due to EHV constraints at 132/33kV Power T/Fs at 132/33kV Amb S/Stn, 132kV D/C Amb-Nehrian line and 220/132kV Nehrian S/Stn.
|  |  |  | 11 kv Ghanari | AAAC 7/4.26, 7/315 mm, 6/1/2.59 mm & 2.11 mm (mixed ) | 1.562 | 0
|  |  |  | 11 kv Ghangret | AAAC 7/4.26, 7/315 mm, 6/1/2.59 mm & 2.11 mm (mixed ) | 1.562 | 0
|  |  |  | 11 kv Chintpurni | AAAC 7/4.26, 7/315 mm, 6/1/2.59 mm & 2.11 mm (mixed ) | 1.562 | 0
|  |  |  | 11 kv Banehra | AAAC 7/4.26, 7/315 mm, 6/1/2.59 mm & 2.11 mm (mixed ) | 1.562 | 0
|  |  |  | 11 kv Marwari | AAAC 7/4.26, 7/315 mm, 6/1/2.59 mm & 2.11 mm (mixed ) | 1.562 | 0
47 | 33/11 kV Sub-Station Bharwain | 6.3 | 0 | 11 KV Bharwain-Chintpurni | AAAC 7/4.26 mm² | 3.9273 | 0 | Capacity exhausted due to EHV constraints at 132/33kV Power T/Fs at 132/33kV Amb S/Stn, 132kV D/C Amb-Nehrian line and 220/132kV Nehrian S/Stn.
|  |  |  | 11 KV Bharwain-Dalwari | AAAC 7/4.26 mm² | 3.9273 | 0
|  |  |  | 11 KV B/D/Shala-Mahanta | AAAC 7/3.15 mm² | 2.7094 | 0
|  |  |  | 11 KV Bharwain-Local | AAAC 7/4.26 mm² | 3.9273 | 0
48 | 33/11 kV Sub-Station Chaksarai | 6.3 | 0 | 11 KV Mairi | AAAC 7/4.26 mm² | 3.9273 | 0 | Capacity exhausted due to EHV constraints at 132/33kV Power T/Fs at 132/33kV Amb S/Stn, 132kV D/C Amb-Nehrian line and 220/132kV Nehrian S/Stn.
|  |  |  | 11KV Rapoh Misran | ACSR 6/1/2.11 mm² | 1.526 | 0
|  |  |  | 11 KV Suri (Jabehar) | AAAC 7/4.26 mm² | 3.9273 | 0
|  |  |  | 11 KV Chaksarai (Local) | ACSR 6/1/2.11 mm² | 1.526 | 0
49 | 33/11 kV Sub-Station Bhaira | 12.6 | 0 | 11 KV Chowkiminar | AAAC 7/4.26 mm² | 3.9273 | 0 | Ram Rattan Vijay Kumar SPP 4 MW thorugh LILOing of 33kV Bhaira-Basal line. Capacity exhausted due to EHV constraints at 132/33kV Power T/Fs at 132/33kV Amb S/Stn, 132kV D/C Amb-Nehrian line and 220/132kV Nehrian S/Stn.
|  |  |  | 11 KV Dhussara | AAAC 7/4.26 mm² | 3.9273 | 0
|  |  |  | 11 KV Bhaira Local | AAAC 7/3.15 mm² | 2.7094 | 0
|  |  |  | 11 Kv Sohari Express | AAAC 7/4.26 mm² | 3.9273 | 0
|  |  |  | 11Kv Chururu Express | AAAC 7/4.26 mm² | 3.9273 | 0
|  |  |  | 11kV Panjawar | ACSR 6/1/4.72 sq mm | 4.098 | 0
|  |  |  | 11 KV Paragoan Express | AAAC 7/4.26 mm² | 3.9273 | 0
50 | 33/11 kV Sub-Station Basal | 12.6 | 0 | 11 KV Takka Feeder | AAAC 7/4.26 and ACSR 6/1/2.11 mm^2 | 1.526 | 0 | Capacity exhausted due to EHV constraints at 132/33kV Power T/Fs at 132/33kV Rakkar (Una) S/Stn, 132kV S/C Amb-Rakkar line, 132kV D/C Amb-Nehrian line and 220/132kV Nehrian S/Stn.
|  |  |  | 11KV Nari Feeder | AAAC 7/4.26 and ACSR 6/1/2.11 mm^2 | 1.526 | 0
|  |  |  | 11 KV Dhamandri Feeder | AAAC 7/4.26 and ACSR 6/1/2.11 mm^2 | 1.526 | 0
|  |  |  | 11 KV Panoh Feeder | AAAC 7/4.26 and ACSR 6/1/2.11 mm^2 | 1.526 | 0
|  |  |  | 11KV Jhalera Feeder | AAAC 7/4.26 and ACSR 6/1/2.11 mm^2 | 1.526 | 0
51 | 33/11 kV Sub-Station Rakkar (UNA) | 12.6 | 0 | UNA- II | AAAC 7/4.26mm,AAAC 7/3.81, AAC 7/3.15 mm | 2.7094 | 0 | Also SPPs with cumulative capacity of 45-48 MW have been granted connectivity in the downstream network and thus 132/33kV Power T/Fs at Rakkar S/Stn are overloaded. Capacity exhausted due to EHV constraints at 132/33kV Power T/Fs at 132/33kV Rakkar (Una) S/Stn, 132kV S/C Amb-Rakkar line, 132kV D/C Amb-Nehrian line and 220/132kV Nehrian S/Stn.
|  |  |  | SAMOOR | AAAC 7/4.26mm, | 3.9273 | 0
|  |  |  | MEHATPUR | ACSR 6/1/3.35, AAAC 7/3.81mm2 | 2.692 | 0
|  |  |  | JHALERA | AAAC 7/4.26mm, AAAC 7/3.81mm2/ AAAC 7/2.50mm | 2.04 | 0
52 | 33/11 kV Sub-Station Pandoga | 12.6 | 0 | 11 kv Pandoga Bharsali feeder | ACSR 6/1/2.11 mm | 1.526 | 0 | Capacity exhausted due to EHV constraints at 132/33kV Power T/Fs at 132/33kV Rakkar (Una) S/Stn, 132kV S/C Amb-Rakkar line, 132kV D/C Amb-Nehrian line and 220/132kV Nehrian S/Stn.
|  |  |  | 11 KV Colony feeder | AAAC 7/4.26 | 3.9273 | 0
|  |  |  | 11 KV Ind Double Circut No.1 | AAAC 7/4.26 | 3.9273 | 0
53 | 33/11 kV Sub-Station Saloh | 3.2 | 0 | 11 KV Saloh Feeder | 7/4.26mm2 | 3.9273 | 0 | Capacity exhausted due to EHV constraints at 132/33kV Power T/Fs at 132/33kV Rakkar (Una) S/Stn, 132kV S/C Amb-Rakkar line, 132kV D/C Amb-Nehrian line and 220/132kV Nehrian S/Stn.
|  |  |  | 11 KV IIIT Feeder | 7/4.26mm2 | 3.9273 | 0
54 | 33/11 kV Sub-Station Thanakalan | 3.2 | 0 | 11KV Ambera Feeder | ACSR 6/1/2.11mm2 | 1.526 | 0 | 4.5 MW + 2.1 MW (Bhubaneswari III) at 33/11kV Thanakalan S/Stn and 10 MW Aghlor SPP through LILO on 33kV Bangana-Rakkar line. Due to line constraints no SPP can be proposed at 33/11kV Thanakalan S/Stn.
|  |  |  | 11KV Raipur Feeder | AAAC 7/3.81mm2, ACSR 6/1/2.11mm2 | 1.526 | 0
|  |  |  | 11KV Khurwain Feeder | ACSR 6/1/2.11mm2 | 1.526 | 0
|  |  |  | 11KV Thanakalan Tihra Feeder | AAAC 7/3.81mm2, AAAC 7/4.26mm2 & ACSR 6/1/2.11mm2 | 1.526 | 0
55 | 33/11 kV Sub-Station Bangana | 6.3 | 0 | 11 KV Jhagrot Feeder | ACSR 6/1/2.59 mm | 1.955 | 0 | 4.5 MW + 2.1 MW (Bhubaneswari III) at 33/11kV Thanakalan S/Stn and 10 MW Aghlor SPP through LILO on 33kV Bangana-Rakkar line. Due to line constraints no SPP can be proposed at 33/11kV Thanakalan S/Stn.
|  |  |  | 11 KV Dhundla Feeder | AAAC 7/4.26 mm, 6/1/2.59 mm | 1.955 | 0
|  |  |  | 11 KV Hatli Feeder | ACSR 6/1/2.59 mm, AAAC 7/4.26 mm | 1.955 | 0
|  |  |  | 11 KV Talmera Feeder | ACSR 6/1/2.59 mm, AAAC 7/4.26 mm | 1.955 | 0
|  |  |  | 11 KV Bangana Feeder | AAAC 7/3.15 mm, AAAC 7/3.81 mm | 2.7094 | 0
|  |  |  | 11 KV Thanakalan Feeder | AAAC 7/4.26 mm, AAAC 7/3.81 mm | 3.412 | 0
|  |  |  | 11 KV Lathaini Feeder | AAAC 7/4.26 mm, ACSR 6/1/2.59 mm | 1.955 | 0
56 | 33/11 kV Sub-Station Santokhgarh | 12.6 | 0 | 11KV Santokhgarh Feeder | (AAAC 7/4.26mm2,AAAC7/3.15mm2,ABCable95mm2,ACSR 6/1/2.59) | 1.955 | 0 | Capacity exhausted due to EHV constraints at 132/33kV Power T/Fs at 132/33kV Rakkar (Una) S/Stn, 132kV S/C Amb-Rakkar line, 132kV D/C Amb-Nehrian line and 220/132kV Nehrian S/Stn.
|  |  |  | 11KV Ajouli Feeder | (AAAC7/4.26mm2,AAAC7/3.81mm2,ACSR 6/1/2.59,ACSR6/1/3.35) | 1.955 | 0
|  |  |  | 11KV Sanouli Feeder | (AAAC 7/3.81mm2,AAAC7/4.26mm2,ACSR6/1/2.59,ACSR6/1/3.35) | 1.955 | 0
|  |  |  | 11KV Nangran Feeder | (ACSR6/1/3.35mm2,AAAC7/4.26mm,ACSR 6/1/2.11AAAC7/3.15mm2) | 1.526 | 0
|  |  |  | 11kV Jankour Feeder | (AAAc7/4.26mm2,AAAC,7/3.81mm2,ACSR6/1/3.35 | 2.692 | 0
57 | 33/11 kV Sub-Station Haroli | 12.6 | 0 | 11 KV Haroli Feeder | 7/4.26mm2, 7/3.15mm2 | 2.7094 | 0 | Capacity exhausted due to EHV constraints at 132/33kV Power T/Fs at 132/33kV Rakkar (Una) S/Stn, 132kV S/C Amb-Rakkar line, 132kV D/C Amb-Nehrian line and 220/132kV Nehrian S/Stn.
|  |  |  | 11 KV Dulehar Feeder | 7/4.26mm2, 7/3.15mm2 | 2.7094 | 0
|  |  |  | 11 KV Tahliwal Rural | 7/4.26mm2, 7/3.15mm2 | 2.7094 | 0
|  |  |  | 11 KV Tahliwal Indust | 7/4.26mm2, 7/3.15mm2 | 2.7094 | 0
|  |  |  | 11 KV Ispur Feeder | 7/4.26mm2, 7/3.15mm2 | 2.7094 | 0
|  |  |  | 11 KV Bhadsali Feeder | 7/4.26mm2, 7/3.15mm2 | 2.7094 | 0
|  |  |  | 11 KV Express Feeder | 7/3.81mm2,7/4.26 | 3.412 | 0
58 | 66/11 kV Sub-Station Rakkar (Una) | 20 | 9.34 | 11KV Una Santokhgarh feeder | AAAC7/4.26mm2,AAAC 7/3.81mm2,11KV XLPE cable 185mm2 | 3.412 | 1.3
|  |  |  | FEEDER NO--1 | AAAC 7/4.26 | 3.9273 | 3.26
|  |  |  | FEEDER NO--3 | AAAC 7/4.26 | 3.9273 | 3.26
|  |  |  | FEEDER NO--4 | AAAC 7/4.26 | 3.9273 | 3.26
|  |  |  | PEERNAGHA | AAAC 7/4.26 | 3.9273 | 2.26
59 | 33/11 kV Sub-Station Mehatpur | 18.9 | 10 | 11KV Tahliwal | ACSR 6/1/4.72mm2 | 4.098 | 2
|  |  |  | 11KV Dehlan | AAAC 7/4.26mm, ACSR 6/1/3.35,AAAC 7/3.81, ACSR 6/1/2.11 | 1.526 | 1
|  |  |  | 11KV S/garh | ACSR 6/1/4.72mm2 | 4.098 | 2
|  |  |  | 11KV Salecha | ACSR 6/1/3.35 | 2.692 | 1.5
|  |  |  | 11KV J.K | ACSR 6/1/3.35 | 2.692 | 1.5
|  |  |  | 11KV Handola | ACSR 6/1/4.72mm,AAAC 7/4.26mm, ACSR 6/1/3.35,AAAC 7/3.81, ACSR 6/1/2.11 | 1.526 | 0
|  |  |  | 11KV Raipur | AAAC 7/4.26mm,AAAC 7/3.81, ACSR 6/1/2.11 | 1.526 | 1
|  |  |  | 11KV Bhabour Sahib | ACSR 6/1/4.72mm, ACSR 6/1/3.35 | 2.692 | 1.5
|  |  |  | 11KV Mehatpur | AAAC 7/4.26mm, ACSR 6/1/3.35 | 2.692 | 1.5
|  |  |  | 11KV Behdala | AAAC 7/4.26mm, ACSR 6/1/3.35,AAAC 7/3.81, ACSR 6/1/2.11 | 1.526 | 0
60 | 132/33/11kV Tahliwal Bathu S/Stn | 20 | 0 | 11kV Bathri-I | ACSR 7/3.81 sqmm | 3.5 | 0 | Capacity exhausted due to EHV constraints at 132kV S/C Amb-Rakkar line, 132kV D/C Amb-Nehrian line and 220/132kV Nehrian S/Stn.
|  |  |  | 11kV Bathri-II | ACSR 7/3.81 sqmm | 3.5 | 0
|  |  |  | 11kV Bathri-III | ACSR 7/3.81 sqmm | 3.5 | 0
|  |  |  | 11kV Bathu | ACSR 7/3.81 sqmm | 3.5 | 0
|  |  |  | 11kV IPH | ACSR 7/3.81 sqmm | 3.5 | 0
61 | 33/11 kV Sub-Station Tahliwal | 18.8 | 0 | 11 KV Tahliwal Bazar | AAAC 7/4.26 mmsq | 3.9273 | 0 | Capacity exhausted due to EHV constraints at 132kV S/C Amb-Rakkar line, 132kV D/C Amb-Nehrian line and 220/132kV Nehrian S/Stn.
|  |  |  | 11 KV Lalheri | AAAC 7/4.26 mmsq,ACSR 6/1/2.59 mmsq ,AAAC 7/3.81 mmsq | 1.955 | 0
|  |  |  | 11 KV Industry Area | AAAC 7/4.26 mmsq | 3.9273 | 0
|  |  |  | 11 KV Dhulehar | AAAC 7/4.26 mmsq | 3.9273 | 0
|  |  |  | 11 KV Gondpur | AAAC 7/4.26 mmsq | 3.9273 | 0
|  |  |  | 11 KV ButtKalan | AAAC 7/4.26 mmsq,AAAC 7/3.15 mmsq,AAAC 7/3.81 mmsq | 2.7094 | 0
62 | 33/11 kV Sub-Station Gondpur | 12.6 | 0 | 11 kv Gondpur-Pubowal Feeder | AAAC 7/4.26 mm | 3.927 | 0 | Capacity exhausted due to EHV constraints at 132kV S/C Amb-Rakkar line, 132kV D/C Amb-Nehrian line and 220/132kV Nehrian S/Stn.
|  |  |  | 11 kv Gondpur-Dulehar Feeder | AAAC 7/4.26 mm | 3.927 | 0
|  |  |  | 11 kv Gondpur-Beetan Feeder | AAAC 7/4.26 mm | 3.927 | 0
|  |  |  | 11 kv Gondpur-Ind No. 1 Singa Feeder | AAAC 7/4.26 mm | 3.927 | 0
|  |  |  | 11 kv Gondpur-Ind No. 2 Feeder | AAAC 7/4.26 mm | 3.927 | 0
| Net Capacity | 551.1 | 127.7884 |  |  |  | 116.6841