## Front Page
COST DATA
33 kV LINES
&
33/11 kV SUB-STATIONS
2012-13

## Assumptions
COST DATA FOR 33kV LINES AND 33/11kV SUB-STATIONS FOR FY- 2012-13.
1 | The cost data for sub-station equipments and material for lines indicates the rates for individual items. The complete estimate for a work shall however be prepared on the basis of actual lay out of the sub-station & other requirements etc.
2 | Cost of civil works for lines, sub-station and equipment has not been incorporated which other wise varies from place to place. The area & site specific conditions shall be taken into account while preparing the estimates.
3 | Cost of land for sub-station and lines which comprises of requirement of land excavation is not envisaged in the cost data and will be incorporated in the estimates as per actual requirements.
4 | The estimates for the works/equipments not specifically covered in the cost data shall be prepared by suitably taking into account the estimated cost of the other similar equipments/ works included in the cost data along with suitable modifications and the effect of other relevant factors specific to the works/ equipment to be estimated.
5 | In case of works awarded on turn-key basis after following the bidding process. The estimates shall be prepared/ revised on the basis of cost as per such awards.
6 | The prices are subject to increase or decrease as per IEEMA formula applicable for the basic raw material i.e. steel, copper, aluminium etc.
7 | The Service Tax and Labour Cess will be payable extra as admissible.
8 | The Labour Rates for erection/manual carriage for the labour hired on daily wages basis in the Scheduled Tribal Areas/ Remote Area/Hard Area as notified by State Government from time to time shall be allowed 25 % enhancement as per the Finance Department's Office Memorandum No. FIN(PR)B(7)-1/95-II dated 17.04.1998.
(i)

## index
Abstract of Cost for 33 kV Lines and 33/11 kV Sub-Stations( FY 2012-13)
S. No | Description | Unit | Rate (Rs. Lacs) | Page No
1 | 33 kV LINE
A) | 33 kV Single Circuit line with 6/1/4.72 mm or 6/1/4.09 ACSR Cond.
(Double Pole Structure) with single continuous earth wire on
I | 9.75mtr . Long PCC Pole (W.L .300 Kg.) | km | 8.0948 | 1
ii | 10 mtr . Long S/T Pole (W.L.300 Kg ) | km | 10.3051 | 1
iii | 60 %9.75mtr . Long PCC Pole & 40% 10 mtr . Long S/T Pole (W.L.300 Kg ) | km | 8.9667 | 1
B) | 33 kV Double Circuit line with 6/1/4.72 mm or 6/1/4.09 ACSR cond. with | km | 14.1819 | 1A
single continuous earth wire on 11 mtr . Long S/T Pole (W.L.300 Kg )
C) | 33 kV Single Circuit line with 7/4.26 mm AAAC cond.
(Double Pole Structure) with single continuous earth wire on
I | 9.75mtr . Long PCC Pole (W.L .300 Kg.) | km | 7.7216 | 2
ii | 10 mtr . Long S/T Pole (W.L.300 Kg ) | km | 9.9319 | 2
iii | 60 %9.75mtr . Long PCC Pole & 40% 10 mtr . Long S/T Pole (W.L.300 Kg ) | km | 8.5935 | 2
D) | 33 kV Double Circuit line with 7/4.26 mm AAAC cond. with | km | 13.3549 | 2A
single continuous earth wire on 11 mtr . Long S/T Pole (W.L.300 Kg )
2 | 33/11 kV Sub-Stations
I | 33/11 kV Sub-Stations incorporating common breaker (Vacuum/SF-6 type ) control for transformer
A) | 2x0.63 MVA, 33/11 kV Sub-Station (Manned) with
1 | 4 nos. out going feeder | No. | 193.2524 | 3
2 | 5 nos. out going feeder | No. | 200.0522 | 3
3 | 6 nos. out going feeder | No. | 206.5704 | 3
4 | 7 nos. out going feeder | No. | 213.3713 | 3
5 | 8 nos. out going feeder | No. | 219.8894 | 3
B) | 2x1.6 MVA , 33/11 kV Sub-Station (Manned) with
1 | 4 nos. out going feeder | No. | 218.8881 | 4
2 | 5 nos. out going feeder | No. | 225.6879 | 4
3 | 6 nos. out going feeder | No. | 232.2061 | 4
4 | 7 nos. out going feeder | No. | 239.007 | 4
5 | 8 nos. out going feeder | No. | 245.5251 | 4
C) | 2x3.15 MVA, 33/11 kV Sub-Station (Manned) with
1 | 4 nos. out going feeder | No. | 230.8543 | 6
2 | 5 nos. out going feeder | No. | 237.6541 | 6
3 | 6 nos. out going feeder | No. | 244.1723 | 6
4 | 7 nos. out going feeder | No. | 250.9732 | 6
5 | 8 nos. out going feeder | No. | 257.4913 | 6
D) | 2x0.63 MVA, 33/11 kV Sub-Station (Un-Manned) with
1 | 4 nos. out going feeder | No. | 205.0028 | 18
2 | 5 nos. out going feeder | No. | 214.6119 | 18
3 | 6 nos. out going feeder | No. | 223.9396 | 18
4 | 7 nos. out going feeder | No. | 233.55 | 18
5 | 8 nos. out going feeder | No. | 242.8777 | 18
E) | 2x1.6 MVA , 33/11 kV Sub-Station (Un-Manned) with
1 | 4 nos. out going feeder | No. | 230.6386 | 19
2 | 5 nos. out going feeder | No. | 240.2477 | 19
3 | 6 nos. out going feeder | No. | 249.5754 | 19
4 | 7 nos. out going feeder | No. | 259.1858 | 19
5 | 8 nos. out going feeder | No. | 268.5135 | 19
(ii)
F) | 2x3.15 MVA, 33/11 kV Sub-Station (Un-Manned) with
1 | 4 nos. out going feeder | No. | 242.6047 | 21
2 | 5 nos. out going feeder | No. | 252.2139 | 21
3 | 6 nos. out going feeder | No. | 261.5416 | 21
4 | 7 nos. out going feeder | No. | 271.152 | 21
5 | 8 nos. out going feeder | No. | 280.4797 | 21
II | 33/11 kV Sub-Stations. Incorporating independent breaker (Vacuum/SF-6 type ) control for transformer
A) | 2x6.3 MVA , 33/11 kV Sub-Station(Manned) with
1 | 4 nos. out going feeder | No. | 270.2799 | 8
2 | 5 nos. out going feeder | No. | 277.0796 | 8
3 | 6 nos. out going feeder | No. | 283.599 | 8
4 | 7 nos. out going feeder | No. | 290.3986 | 8
5 | 8 nos. out going feeder | No. | 296.9168 | 8
B) | 1x3.15 MVA, 33/11 kV Sub-Station (Manned) with
1 | 4 nos. out going feeder | No. | 188.8185 | 7
2 | 5 nos. out going feeder | No. | 195.6182 | 7
3 | 6 nos. out going feeder | No. | 202.1375 | 7
4 | 7 nos. out going feeder | No. | 208.9373 | 7
5 | 8 nos. out going feeder | No. | 215.4555 | 7
C) | 1x1.6 MVA 33/11 kV Sub-Station (Manned) with
1 | 4 nos. out going feeder | No. | 182.8354 | 5
2 | 5 nos. out going feeder | No. | 189.6351 | 5
3 | 6 nos. out going feeder | No. | 196.1544 | 5
4 | 7 nos. out going feeder | No. | 202.9542 | 5
5 | 8 nos. out going feeder | No. | 209.4724 | 5
D) | 2x6.3 MVA , 33/11 kV Sub-Station(Un-Manned) with
1 | 4 nos. out going feeder | No. | 275.6243 | 23
2 | 5 nos. out going feeder | No. | 285.2334 | 23
3 | 6 nos. out going feeder | No. | 294.5622 | 23
4 | 7 nos. out going feeder | No. | 304.1715 | 23
5 | 8 nos. out going feeder | No. | 313.4992 | 23
E) | 1x3.15 MVA, 33/11 kV Sub-Station (Un-Manned) with
1 | 4 nos. out going feeder | No. | 197.3659 | 22
2 | 5 nos. out going feeder | No. | 206.975 | 22
3 | 6 nos. out going feeder | No. | 216.3038 | 22
4 | 7 nos. out going feeder | No. | 225.9131 | 22
5 | 8 nos. out going feeder | No. | 235.2408 | 22
F) | 1x1.6 MVA 33/11 kV Sub-Station (Un-Manned) with
1 | 4 nos. out going feeder | No. | 191.3828 | 20
2 | 5 nos. out going feeder | No. | 200.9919 | 20
3 | 6 nos. out going feeder | No. | 210.3207 | 20
4 | 7 nos. out going feeder | No. | 219.93 | 20
5 | 8 nos. out going feeder | No. | 229.2577 | 20
3 | Terminal equipment for each of 33 kV out going feeder from Sub-Station
(with Vacuum/SF-6 C.B.) where
a | 33/11 kV where PT's exists. | No. | 11.4551 | 52
b | 33/11 kV where PT's do not exists | No. | 12.4887 | 52
4 | Installation of 11 kV Auto Voltage Booster
a | Out door type 100 Amps rating | No. | 12.9831 | 55
5 | Installation of 11 kV Auto Reclosure / line sectionalizer.
a | Auto reclosure | No. | 6.6901 | 57
b | Line sectionalizer | No. | 4.6422 | 57
6 | Installation of 11 kV Shunt Capacitor Bank with rating.
a | 1.2 MVAR | No. | 7.3755 | 60
b | 1.8 MVAR | No. | 9.9737 | 60
(iii)

## page 1-2
Page -1
Cost Data for Construction of one km of 33 kV Single Circuit (S/C) Double Pole Structures line with
ACSR 6/1/4.72 mm Conductor (100 mm2. Eq. for wind pressure Zone upto 150 kg / M 2) on 9.75 mtr./10 mtr.
Long PCC Poles, Steel Tubular Poles and 60 % PCC & 40 % ST Poles with single continuous earth wire
S. | Description of item | ISS.No. | Unit | Qty | Rate | Amount in Rs.
No. |  | REC STD |  |  | Rs. | PCC | S/T | 60 % PCC
|  | No. |  |  |  | Pole | Pole | & 40 % S/T
Poles
1 | Material for surveying and stacking of line (1 km)
a | Wooden pegs |  | No. | 12 | 23 | 276 | 276 | 276
b | Stone pillar/RCC pillars with one wastage |  | No. | 7 | 1049 | 7343 | 7343 | 7343
2 | PCC poles 9.75 mtr. Long (Working.Load. 300 kg) | 1678/1978 | No. | 20 | 2759 | 55180
3 | S/T poles,10 mtr.,with pole cap (Working.Load. 300 kg) | 2713/1980 | No. | 20 | 11963 |  | 239260
4 | 60 % PCC & 40 %S/T poles |  | No. | 20 | 6440.6 |  |  | 128812
5 | Muffs |  | No. | 20 | 690 |  | 13800 | 5520
6 | Angle iron 2240*65*65*6 mm cross arm for earth wires |  | No. | 10 | 776 | 7760 | 7760 | 7760
7 | M.S. cross bracing set (consisting of one1800x65X65x6 mm- 2 Nos |  | No. | 10 | 2486 | 24860 | 24860 | 24860
and 2700x50x50x6 mm-2 Nos. os M.S Angle irons including
clamps and bolts.)
8 | M.S. channel iron cross arm (4000x125x65x6 mm for |  | No. | 12 | 2670 | 32040 | 32040 | 32040
8 Nos. suspension structure=8 Nos. and 2 Nos.for dead
end structure each= 4 Nos.)
9 | Half clamps |  | No. | 34 | 127 | 4318 | 4318 | 4318
10 | Nuts and Bolts of Various Sizes |  | Kg | 75 | 68 | 5100 | 5100 | 5100
11 | Stay set complete (2 nos.for suspension structures with |  | No. | 15 | 1919 | 28785 | 28785 | 28785
angle & 1 no. dead end with angle)
12 | Stay Wire 7/4.00 mm ( @ 9.0 kg Per Stay Set) |  | Kg | 135 | 58 | 7830 | 7830 | 7830
13 | 33 kV Pin Insulators alongwith Pin |  | No. | 15 | 384 | 5760 | 5760 | 5760
( on 2 Nos. Dead End structure and 3 NosTangent Structure)
14 | Three discs insulator suspension string (P-54) |  | No. | 27 | 1553 | 41931 | 41931 | 41931
(on 5 Nos suspension Str. And 2 Nos Dead End Structure)
15 | Earth Reel |  | No. | 10 | 18 | 180 | 180 | 180
16 | Barbed wire |  | Kg. | 80 | 58 | 4640 | 4640 | 4640
17 | Danger plate (203X200X1.6mm) |  | No. | 10 | 101 | 1010 | 1010 | 1010
18 | HT Earthing set |  | No. | 10 | 1153 | 11530 | 11530 | 11530
19 | Material for 2 nos. road, path/road guarding in 1 km of line
a | PCC poles 8 mtr. Long | 1678/1978 | No. | 4 | 1754 | 7016 | 7016 | 7016
b | Stay set LT |  | No. | 4 | 873 | 3492 | 3492 | 3492
c | Stay Wire 7/3.15 mm ( @ 6.0 kg Per Stay Set) |  | kg | 24 | 59 | 1416 | 1416 | 1416
d | Earthing set |  | No. | 2 | 689 | 1378 | 1378 | 1378
e | Catenary wire |  | mtr. | 30 | 59 | 1770 | 1770 | 1770
f | Cross Arm ( 2 Nos of Angle iron 2240*65*65*6 mm) |  | No. | 2 | 776 | 1552 | 1552 | 1552
g | Half clamps |  | No. | 2 | 127 | 254 | 254 | 254
20 | GI wire no. 6 SWG for earth wire sag & wastage | 280/1978 | kg | 155 | 59 | 9145 | 9145 | 9145
= 1.03 km @ 150 kg/km
21 | ACSR 6/1/4.72 including 3 % sag and wastage |  | km | 3.09 | 55400 | 171186 | 171186 | 171186
|  | S/Total |  |  |  | 435752 | 633632 | 514904
| Storage Charges @ 3.0 % |  |  |  |  | 13072.56 | 19008.96 | 15447.12
| Contingencies Charges @ 3.0 % |  |  |  |  | 13072.56 | 19008.96 | 15447.12
| Transportation Charges as per statement (P-61) |  |  |  |  | 48480 | 34850 | 43030
| Erection charges as per statement (P-73) |  |  |  |  | 218880 | 221890 | 218986
|  | Total |  |  |  | 729257.12 | 928389.92 | 807814.24
| Departmental Charges @ 11.0 % |  |  |  |  | 80218.2832 | 102122.8912 | 88859.5664
|  | Grand Total |  |  |  | 809475.4032 | 1030512.8112 | 896673.8064
|  | Say Rs. In lacs |  |  |  | 8.0948 | 10.3051 | 8.9667 | 8.9963
Page-2
Cost Data for Construction of one km of 33 kV Single Circuit (S/C) Double Pole Structures line with
AAAC 7/4.26 mm Conductor (100 mm2 Eq. for wind pressure Zone upto 150 kg / M 2) on 9.75 mtr./10 mtr.
Long PCC Poles, Steel Tubular Poles and 60 % PCC & 40 % ST Poles with single continuous earth wire
S. | Description of item | Iss.No. | Unit | Qty | Rate | Amount in Rs.
No. |  | REC STD |  |  | Rs. | PCC | S/T | 60 % PCC
|  | No. |  |  |  | pole | pole | & 40 % S/T
Poles
1 | Material for surveying and stacking of 33 KV line (1 km)
a | Wooden pegs |  | No. | 12 | 23 | 276 | 276 | 276
b | Stone pillar/RCC pillars with one wastage |  | No. | 7 | 1049 | 7343 | 7343 | 7343
2 | PCC poles 9.75 mtr. Long (Working Load 300 kg) | 1678/1978 | No. | 20 | 2759 | 55180
3 | S/T poles,10 mtr. with pole cap (Working Load 300 kg) | 2713/1980 | No. | 20 | 11963 |  | 239260
4 | 60 % PCC & 40 %S/T poles |  | No. | 20 | 6440.6 |  |  | 128812
5 | Muffs |  | No. | 20 | 690 |  | 13800 | 5520
6 | Angle iron 2240*65*65*6 mm cross arm for earth wires |  | No. | 10 | 776 | 7760 | 7760 | 7760
7 | M.S. cross bracing set (consisting of one1800x65X65x6 mm- 2 Nos |  | No. | 10 | 2486 | 24860 | 24860 | 24860
and 2700x50x50x6 mm-2 Nos. os M.S Angle irons including
clamps and bolts.)
8 | M.S. channel iron cross arm (4000x125x65x6 mm for |  | No. | 12 | 2670 | 32040 | 32040 | 32040
8 Nos. suspension structure=8 Nos. and 2 Nos.for dead
end structure each= 4 Nos.)
9 | Half clamps |  | No. | 34 | 127 | 4318 | 4318 | 4318
10 | Nuts and Bolts of Various Sizes |  | Kg | 75 | 68 | 5100 | 5100 | 5100
11 | Stay set complete (2 nos.for suspension structures with |  | No. | 15 | 1919 | 28785 | 28785 | 28785
angle & 1 no. dead end with angle)
12 | Stay Wire 7/4.00 mm ( @ 9.0 kg Per Stay Set) |  | Kg | 135 | 58 | 7830 | 7830 | 7830
13 | 33 kV Pin Insulators alongwith Pin |  | No. | 15 | 384 | 5760 | 5760 | 5760
( on 2 Nos. Dead End structure and 3 NosTangent Structure)
14 | Three discs insulator suspension string (P-54) |  | No. | 27 | 1553 | 41931 | 41931 | 41931
(on 5 Nos suspension Str. And 2 Nos Dead End Structure)
15 | Earth reel |  | No. | 10 | 18 | 180 | 180 | 180
16 | Barbed wire |  | Kg. | 80 | 58 | 4640 | 4640 | 4640
17 | Danger plate |  | No. | 10 | 101 | 1010 | 1010 | 1010
18 | HT Earthing set |  | No. | 10 | 1153 | 11530 | 11530 | 11530
19 | Material for 2 nos. road, path/road guarding in 1 km of line
a | PCC poles 8 mtr. Long | 1678/1978 | No. | 4 | 1754 | 7016 | 7016 | 7016
b | Stay set LT |  | No. | 4 | 873 | 3492 | 3492 | 3492
c | Stay Wire 7/3.15 mm ( @ 6.0 kg Per Stay Set) |  | kg | 24 | 59 | 1416 | 1416 | 1416
d | Earthing set |  | No. | 4 | 689 | 2756 | 2756 | 2756
e | Catenary wire |  | mtr. | 30 | 59 | 1770 | 1770 | 1770
f | Cross Arm ( 2 Nos of Angle iron 2240*65*65*6 mm) |  | No. | 2 | 776 | 1552 | 1552 | 1552
g | Half clamps |  | No. | 2 | 127 | 254 | 254 | 254
20 | GI wire no. 6 SWG for earth wire | 280/1978 | kg | 155 | 59 | 9145 | 9145 | 9145
sag & wastage =1.03 km @ 150 kg/km
21 | AAAC 7/4.26 including 3 % sag and wastage |  | km | 3.09 | 44785 | 138385.65 | 138385.65 | 138385.65
|  | S/Total |  |  |  | 404329.65 | 602209.65 | 483481.65
| Storage Charges @ 3.0 % |  |  |  |  | 12129.8895 | 18066.2895 | 14504.4495
| Contingencies Charges @ 3.0 % |  |  |  |  | 12129.8895 | 18066.2895 | 14504.4495
| Transportation charges as per statement (P-61) |  |  |  |  | 48170 | 34530 | 42710
| Erection charges as per statement (P-73) |  |  |  |  | 218880 | 221890 | 218986
|  | Total |  |  |  | 695639.429 | 894762.229 | 774186.549
| Departmental charges @ 11.0 % |  |  |  |  | 76520.3372 | 98423.8452 | 85160.5204
|  | Grand Total |  |  |  | 772159.7662 | 993186.0742 | 859347.0694
|  | Say Rs. In lacs |  |  |  | 7.7216 | 9.9319 | 8.5935
Page -1A
Cost Data for Construction of one km of 33 KV Double Circuit (D/C) Double Pole Structures line with
ACSR 6/1/4.72mm conductor (100 mm2 Equivalent for wind pressure Zone upto 150 kg / M 2)
on 11 mtr. Long Steel Tubular Pole with single continuous earth wire
S. | Description of item | ISS.No. | Unit | Qty | Rate | Amount in Rs.
No. |  | REC STD |  |  | Rs. |  | S/T
|  | No. |  |  |  |  | pole
1 | Material for surveying and stacking of line (1 km)
a | Wooden pegs |  | No. | 12 | 23 |  | 276
b | Stone pillar/RCC pillars with one wastage |  | No. | 7 | 1049 |  | 7343
2 | S/T poles,11 mtr. with pole cap (Working.Load. 300 kg) | 2713/1980 | No. | 20 | 12881 |  | 257620
3 | Muffs |  | No. | 20 | 690 |  | 13800
4 | Angle iron 2240*65*65*6 mm cross arm for earth wires |  | No. | 10 | 776 |  | 7760
5 | M.S. cross bracing set (consisting of one1800x65X65x6 mm- 2 Nos |  | No. | 10 | 2486 |  | 24860
and 2700x50x50x6 mm-2 Nos. os M.S Angle irons including
clamps and bolts.)
6 | M.S. channel iron cross arm (4000x125x65x6 mm for |  | No. | 24 | 2670 |  | 64080
8 Nos. suspension structure=8 Nos. and 2 Nos.for dead
end structure each= 4 Nos.)
7 | Half clamps |  | No. | 58 | 127 |  | 7366
8 | Nuts and Bolts of Various Sizes |  | Kg | 100 | 68 |  | 6800
9 | Stay set complete (2 nos.for suspension structures with |  | No. | 15 | 1919 |  | 28785
angle & 1 no. dead end with angle)
10 | Stay Wire 7/4.00 mm ( @ 9.0 kg Per Stay Set) |  | Kg | 135 | 58 |  | 7830
11 | 33 kV Pin Insulators alongwith Pin |  | No. | 30 | 384 |  | 11520
( on 2 Nos. Dead End structure and 3 NosTangent Structure)
12 | Three discs insulator suspension string (P-54) |  | No. | 54 | 1553 |  | 83862
(on 5 Nos suspension Str. And 2 Nos Dead End Structure)
13 | Earth reel |  | No. | 10 | 18 |  | 180
14 | Barbed wire |  | Kg. | 80 | 58 |  | 4640
15 | Danger plate |  | No. | 10 | 101 |  | 1010
16 | HT Earthing set |  | No. | 10 | 1153 |  | 11530
17 | Material for 2 nos. road, path/road guarding in 1 km of line
a | PCC poles 8 mtr. Long | 1678/1978 | No. | 4 | 1754 |  | 7016
b | Stay set LT |  | No. | 4 | 873 |  | 3492
c | Stay Wire 7/3.15 mm ( @ 6.0 kg Per Stay Set) |  | kg | 24 | 59 |  | 1416
d | Earthing set |  | No. | 2 | 689 |  | 1378
e | Catenary wire |  | mtr. | 30 | 58 |  | 1740
f | Cross Arm ( 2 Nos of Angle iron 2240*65*65*6 mm) |  | No. | 2 | 776 |  | 1552
g | Half clamps |  | No. | 2 | 127 |  | 254
18 | GI wire no. 6 SWG for earth wire | 280/1978 | kg | 155 | 59 |  | 9145
sag & wastage =1.03 km @ 150 kg/km
19 | ACSR 6/1/4.72including 3 % sag and wastage |  | km | 6.18 | 55400 |  | 342372
|  | S/Total |  |  |  |  | 907627
| Storage Charges @ 3.0 % | [5 empty] | 27228.81
| Contingencies Charges @ 3.0 % | [5 empty] | 27228.81
| Transportation charges as per statement (P-61) | [5 empty] | 34850
| Erection charges as per statement (P-73) | [5 empty] | 280710
|  | Total |  |  |  |  | 1277644.62
| Departmental charges @ 11.0 % | [5 empty] | 140540.9082
|  | Grand Total |  |  |  |  | 1418185.5282
|  | Say Rs. In lacs |  |  |  |  | 14.1819
Page-2A
Cost Data for Construction of one km of 33 KV Double Circuit (D/C) Double Pole Structures line with
AAAC 7/4.26 mm conductor (100 mm2 Equivalent for wind pressure Zone upto 150 kg / M 2)
on 11 mtr. Long Steel Tubular Pole with single continuous earth wire
S. | Description of item | Iss.No. | Unit | Qty | Rate | Amount in Rs.
No. |  | REC STD |  |  | Rs. |  | Steel Pole
No.
1 | Material for surveying and stacking of 33 KV line (1 km)
a | Wooden pegs |  | No. | 12 | 23 |  | 276
b | Stone pillar/RCC pillars with one wastage |  | No. | 7 | 1049 |  | 7343
2 | S/T poles,11 mtr.with pole cap (Working Load 300 kg) | 2713/1980 | No. | 20 | 12881 |  | 257620
3 | Muffs |  | No. | 20 | 690 |  | 13800
4 | Angle iron 2240*65*65*6 mm cross arm for earth wires |  | No. | 10 | 776 |  | 7760
5 | M.S. cross bracing set (consisting of one1800x65X65x6 mm- 2 Nos |  | No. | 10 | 2486 |  | 24860
and 2700x50x50x6 mm-2 Nos. os M.S Angle irons including
clamps and bolts.)
6 | M.S. channel iron cross arm (4000x125x65x6 mm for |  | No. | 24 | 2670 |  | 64080
8 Nos. suspension structure=8 Nos. and 2 Nos.for dead
end structure each= 4 Nos.)
7 | Half clamps |  | No. | 58 | 127 |  | 7366
8 | Nuts and Bolts of Various Sizes |  | Kg | 100 | 68 |  | 6800
9 | Stay set complete (2 nos.for suspension structures with |  | No. | 15 | 1919 |  | 28785
angle & 1 no. dead end with angle)
10 | Stay Wire 7/4.00 mm ( @ 9.0 kg Per Stay Set) |  | Kg | 135 | 58 |  | 7830
11 | 33 kV Pin Insulators alongwith Pin |  | No. | 15 | 384 |  | 5760
( on 2 Nos. Dead End structure and 3 NosTangent Structure)
12 | Three discs insulator suspension string (P-54) |  | No. | 54 | 1553 |  | 83862
(on 5 Nos suspension Str. And 2 Nos Dead End Structure)
13 | Earth Reel |  | No. | 10 | 18 |  | 180
14 | Barbed wire |  | Kg. | 80 | 58 |  | 4640
15 | Danger plate |  | No. | 10 | 101 |  | 1010
16 | HT Earthing set |  | No. | 10 | 1153 |  | 11530
17 | Material for 2 nos. road, path/road guarding in 1 km of line
a | PCC poles 8 mtr. Long | 1678/1978 | No. | 4 | 1754 |  | 7016
b | Stay set LT |  | No. | 4 | 873 |  | 3492
c | Stay Wire 7/3.15 mm ( @ 6.0 kg Per Stay Set) |  | kg | 24 | 59 |  | 1416
d | Earthing set |  | No. | 4 | 689 |  | 2756
e | Catenary wire |  | mtr. | 30 | 58 |  | 1740
f | Cross Arm ( 2 Nos of Angle iron 2240*65*65*6 mm) |  | No. | 2 | 776 |  | 1552
g | Half clamps |  | No. | 2 | 127 |  | 254
18 | GI wire no. 6 SWG for earth wire | 280/1978 | kg | 155 | 59 |  | 9145
sag & wastage =1.03 km @ 150 kg/km
19 | AAAC 7/4.26 including 3 % sag and wastage |  | km | 6.18 | 44785 |  | 276771.3
|  | S/Total |  |  |  |  | 837644.3
| Storage Charges @ 3.0 % | [5 empty] | 25129.329
| Contingencies Charges @ 3.0 % | [5 empty] | 25129.329
| Transportation charges as per statement (P-61) | [5 empty] | 34530
| Erection charges as per statement (P-73) | [5 empty] | 280710
|  | Total |  |  |  |  | 1203142.958
| Departmental charges @ 11.0 % | [5 empty] | 132345.7254
|  | Grand Total |  |  |  |  | 1335488.6834
|  | Say Rs. In lacs |  |  |  |  | 13.3549

## page 3-17
PAGE- 3
Cost of 2x 0.63 MVA, 33 kV Terminal Equipment & Sub-Station (Manned) with 4 to 8 nos. of out going Feeders
with Common Breaker ( vacuum/SF6 ) Control for Transformer
S.No. | Description of item | ISS.No. | Unit | Qty | Rate | Amount for Sub-Station With No. of out going Feeders.
|  | REC Std. No |  |  | Rs. | 4 Nos. | 5 Nos. | 6 Nos. | 7 Nos. | 8 Nos.
1 | Cost of Terminal Equipments for 2x 0.63 MVA,33/11 kV Sub-Station |  | No. | 1 | -- | 7469590 | 7912130 | 8330740 | 8773280 | 9191880
with 4 to 8 nos. out going feeder excluding the cost of Power Transformer
& 11 kV incoming cable (P- 9 to 11)
2 | 0.63 MVA, 33/11 kV Transformer | 2026/1993 | No. | 2 | 887500 | 1775000 | 1775000 | 1775000 | 1775000 | 1775000
3 | 95 mm2. 11 kV grade cable | 7098/1985 | Mtr | 100 | 697 | 69700 | 69700 | 69700 | 69700 | 69700
|  |  | S/Total |  |  | 9314290 | 9756830 | 10175440 | 10617980 | 11036580
| Storage Charges @ 3.0 % |  |  |  |  | 279428.7 | 292704.9 | 305263.2 | 318539.4 | 331097.4
| Contingencies Charges @ 3.0 % |  |  |  |  | 279428.7 | 292704.9 | 305263.2 | 318539.4 | 331097.4
| Transportation charges as per statement (P-61) |  |  |  |  | 312900 | 312900 | 312900 | 312900 | 312900
| Erection charges as per statement(P-75) |  |  |  |  | 3965200 | 4108700 | 4252200 | 4395800 | 4539300
| Cost of control room building as per detail(P-51) |  |  |  |  | 3258877 | 3258877 | 3258877 | 3258877 | 3258877
|  |  | Total |  |  | 17410124.4 | 18022716.8 | 18609943.4 | 19222635.8 | 19809851.8
| Departmental charges @ 11.0 % |  |  |  |  | 1915113.684 | 1982498.848 | 2047093.774 | 2114489.938 | 2179083.698
|  |  | Grand Total |  |  | 19325238.084 | 20005215.648 | 20657037.174 | 21337125.738 | 21988935.498
|  |  | Say Rs. In lacs |  |  | 193.2524 | 200.0522 | 206.5704 | 213.3713 | 219.8894
PAGE-4
Cost of 2x1.6 MVA, 33 kV Terminal Equipment & Sub-Station (Manned) with 4 to 8 nos. of out going Feeders
with Common Breaker ( vacuum/SF6 ) Control for Transformer
S.No. | Description of item | ISS.No. | Unit | Qty | Rate | Amount for Sub-Station With No. of out going Feeders.
|  | REC Std. No |  |  | Rs. | 4 Nos. | 5 Nos. | 6 Nos. | 7 Nos. | 8 Nos.
1 | Cost of Terminal Equipments for 2x 1.6 MVA,33/11 kV Substation |  | No. | 1 | -- | 7469590 | 7912130 | 8330740 | 8773280 | 9191880
with 4 to 8 nos. out going Feeder excluding the cost of Power Transformer
& 11 kV incoming cable (P- 9 to 11)
2 | 1.6 MVA, 33/11 kV Transformer | 2026/1993 | No. | 2 | 1963500 | 3927000 | 3927000 | 3927000 | 3927000 | 3927000
3 | 120 mm2. 11 kV grade cable | 7098/1985 | No. | 100 | 965 | 96500 | 96500 | 96500 | 96500 | 96500
|  |  | S/Total |  |  | 11493090 | 11935630 | 12354240 | 12796780 | 13215380
| Storage Charges @ 3.0 % |  |  |  |  | 344793 | 358069 | 370627 | 383903 | 396461
| Contingencies Charges @ 3.0 % |  |  |  |  | 344793 | 358069 | 370627 | 383903 | 396461
| Transportation charges as per statement (P-61) |  |  |  |  | 312900 | 312900 | 312900 | 312900 | 312900
| Erection charges as per statement(P-75) |  |  |  |  | 3965200 | 4108700 | 4252200 | 4395800 | 4539300
| Cost of control room building as per detail (P-51) |  |  |  |  | 3258877 | 3258877 | 3258877 | 3258877 | 3258877
|  |  | Total |  |  | 19719653 | 20332245 | 20919471 | 21532163 | 22119379
| Departmental Charges @ 11.0 % |  |  |  |  | 2169161.83 | 2236546.95 | 2301141.81 | 2368537.93 | 2433131.69
|  |  | Grand Total |  |  | 21888814.83 | 22568791.95 | 23220612.81 | 23900700.93 | 24552510.69
|  |  | Say Rs. In lacs |  |  | 218.8881 | 225.6879 | 232.2061 | 239.007 | 245.5251
PAGE-5
Cost of 1x1.6 MVA, Terminal Equipment & Sub-Station (Manned) with 4 to 8 nos. out going Feeders
with Independent Breaker ( vacuum/SF6 ) Control for Transformer
S.No. | Description of item | ISS.No. | Unit | Qty | Rate | Amount for Sub-Station With No. of out going Feeders.
|  | REC Std. No |  |  |  | 4 Nos. | 5 Nos. | 6 Nos. | 7 Nos. | 8 Nos.
1 | Cost of Terminal Equipments for 1x1.6 MVA,33/11 kV Sub-Station |  | No. | 1 |  | 6403140 | 6845670 | 7264280 | 7706820 | 8125430
with 4 to 8 nos. out going Feeder excluding the cost of Power Transformer
& 11 kV incoming cable (P- 12 to 14)
2 | 1.6 MVA, 33/11 kV Transformer | 2026/1993 | No. | 1 | 1963500 | 1963500 | 1963500 | 1963500 | 1963500 | 1963500
3 | 120 mm2. 11 kV grade cable | 7098/1985 | No. | 50 | 965 | 48250 | 48250 | 48250 | 48250 | 48250
|  |  | S/Total |  |  | 8414890 | 8857420 | 9276030 | 9718570 | 10137180
| Storage Charges @ 3.0 % |  |  |  |  | 252447 | 265723 | 278281 | 291557 | 304115
| Contingencies Charges @ 3.0 % |  |  |  |  | 252447 | 265723 | 278281 | 291557 | 304115
| Transportation charges as per statement (P-61) |  |  |  |  | 312900 | 312900 | 312900 | 312900 | 312900
| Erection charges as per statement(P-75) |  |  |  |  | 3980100 | 4123600 | 4267200 | 4410700 | 4554200
| Cost of control room building as per detail(P-51) |  |  |  |  | 3258877 | 3258877 | 3258877 | 3258877 | 3258877
|  |  | Total |  |  | 16471661 | 17084243 | 17671569 | 18284161 | 18871387
| Departmental Charges @ 11 % |  |  |  |  | 1811882.71 | 1879266.73 | 1943872.59 | 2011257.71 | 2075852.57
|  |  | Grand Total |  |  | 18283543.71 | 18963509.73 | 19615441.59 | 20295418.71 | 20947239.57
|  |  | Say Rs. In lacs |  |  | 182.8354 | 189.6351 | 196.1544 | 202.9542 | 209.4724
PAGE-6
Cost of 2x3.15 MVA, 33 kV Terminal Equipment & Sub-Station (Manned) with 4 to 8 nos. out going Feeders
with Common Breaker ( vacuum/SF6 ) Control for Transformer
S.No. | Description of item | ISS.No. | Unit | Qty | Rate | Amount for Sub-Station With No. of out going Feeders.
|  | REC Std. No |  |  | Rs. | 4 Nos. | 5 Nos. | 6 Nos. | 7 Nos. | 8 Nos.
1 | Cost of Terminal Equipments for 2x 3.15 MVA,33/11 kV Sub-Station |  | No. | 1 | -- | 7469590 | 7912130 | 8330740 | 8773280 | 9191880
with 4 to 8 nos. out going Feeder excluding the cost of Power Transformer
&11 kV incoming cable (P- 9 to 11)
2 | 3.15 MVA, 33/11 kV Transformer | 2026/1992 | No. | 2 | 2472007 | 4944014 | 4944014 | 4944014 | 4944014 | 4944014
3 | 185 mm2. 11 kV grade cable | 7098/1985 | Mtr | 100 | 965 | 96500 | 96500 | 96500 | 96500 | 96500
|  |  | S/Total |  |  | 12510104 | 12952644 | 13371254 | 13813794 | 14232394
| Storage Charges @ 3.0 % |  |  |  |  | 375303 | 388579 | 401138 | 414414 | 426972
| Contingencies Charges @ 3.0 % |  |  |  |  | 375303 | 388579 | 401138 | 414414 | 426972
| Transportation charges as per statement (P-61) |  |  |  |  | 312900 | 312900 | 312900 | 312900 | 312900
| Erection charges as per statement(P-75) |  |  |  |  | 3965200 | 4108700 | 4252200 | 4395800 | 4539300
| Cost of control room building as per detail(P-51) |  |  |  |  | 3258877 | 3258877 | 3258877 | 3258877 | 3258877
|  |  | Total |  |  | 20797687 | 21410279 | 21997507 | 22610199 | 23197415
| Departmental Charges @ 11.0 % |  |  |  |  | 2287745.57 | 2355130.69 | 2419725.77 | 2487121.89 | 2551715.65
|  |  | Grand Total |  |  | 23085432.57 | 23765409.69 | 24417232.77 | 25097320.89 | 25749130.65
|  |  | Say Rs. In lacs |  |  | 230.8543 | 237.6541 | 244.1723 | 250.9732 | 257.4913
PAGE-7
Cost of 1x3.15 MVA, Terminal Equipment & Sub-Station (Manned) with 4 to 8 nos. out going Feeders
with Independent Breaker ( vacuum/SF6 ) Control for Transformer
S.No. | Description of item | ISS.No. | Unit | Qty | Rate | Amount for Sub-Station With No. of out going Feeders.
|  | REC Std. No |  |  |  | 4 Nos. | 5 Nos. | 6 Nos. | 7 Nos. | 8 Nos.
1 | Cost of Terminal Equipments for 1x3.15MVA,33/11 kV Sub-Station |  | No. | 1 | -- | 6403140 | 6845670 | 7264280 | 7706820 | 8125430
with 4 to 8 nos. out going Feeder excluding the cost of Power Transformer
& 11 kV incoming cable (P- 12 to 14)
2 | 3.15 MVA, 33/11 kV Transformer | 2026/1993 | No. | 1 | 2472007 | 2472007 | 2472007 | 2472007 | 2472007 | 2472007
3 | 185 mm2. 11 kV grade cable | 7098/1985 | No. | 50 | 965 | 48250 | 48250 | 48250 | 48250 | 48250
|  |  | S/Total |  |  | 8923397 | 9365927 | 9784537 | 10227077 | 10645687
| Storage Charges @ 3.0 % |  |  |  |  | 267701.91 | 280977.81 | 293536.11 | 306812.31 | 319370.61
| Contingencies Charges @ 3.0 % |  |  |  |  | 267701.91 | 280977.81 | 293536.11 | 306812.31 | 319370.61
| Transportation charges as per statement (P-61) |  |  |  |  | 312900 | 312900 | 312900 | 312900 | 312900
| Erection charges as per statement(P-75) |  |  |  |  | 3980100 | 4123600 | 4267200 | 4410700 | 4554200
| Cost of control room building as per detail(P-51) |  |  |  |  | 3258877 | 3258877 | 3258877 | 3258877 | 3258877
|  |  | Total |  |  | 17010677.82 | 17623259.62 | 18210586.22 | 18823178.62 | 19410405.22
| Departmental charges @ 11.0 % |  |  |  |  | 1871174.5602 | 1938558.5582 | 2003164.4842 | 2070549.6482 | 2135144.5742
|  |  | Grand Total |  |  | 18881852.3802 | 19561818.1782 | 20213750.7042 | 20893728.2682 | 21545549.7942
|  |  | Say Rs. In lacs |  |  | 188.8185 | 195.6182 | 202.1375 | 208.9373 | 215.4555
PAGE-8
Cost of 2x6.3 MVA, 33 kV Terminal Equipment & Sub-Station ( Manned) with 4 to 8 nos. out going Feeders and
incorporating independent breaker ( vacuum/SF6 ) control for Transformer
S.No. | Description of item | ISS.No. | Unit | Qty | Rate | Amount for Sub-Station With No. of out going Feeders.
|  | REC Std. No |  |  | Rs. | 4 Nos. | 5 Nos. | 6 Nos. | 7 Nos. | 8 Nos.
1 | Cost of Terminal Equipments for 2x 6.3MVA,33/11 kV Sub-Station |  | No. | 1 | -- | 8428280 | 8870820 | 9289430 | 9731960 | 10150570
with 4 to 8 nos. out going Feeder excluding the cost of Power Transformer
&11 kV incoming cable (P- 15 to 17)
2 | 6.3 MVA, 33/11 kV Transformer | 2026 | No. | 2 | 3642385 | 7284770 | 7284770 | 7284770 | 7284770 | 7284770
3 | 240 mm2. 11 kV grade cable | 7098/1985 | No. | 100 | 1338 | 133800 | 133800 | 133800 | 133800 | 133800
|  |  | S/Total |  |  | 15846850 | 16289390 | 16708000 | 17150530 | 17569140
| Storage Charges @ 3.0 % |  |  |  |  | 475405.5 | 488681.7 | 501240 | 514515.9 | 527074.2
| Contingencies Charges @ 3.0 % |  |  |  |  | 475405.5 | 488681.7 | 501240 | 514515.9 | 527074.2
| Transportation charges as per statement (P-61) |  |  |  |  | 312900 | 312900 | 312900 | 312900 | 312900
| Erection charges as per statement(P-75) |  |  |  |  | 3980100 | 4123600 | 4267200 | 4410700 | 4554200
| Cost of control room building as per detail(P-51) |  |  |  |  | 3258877 | 3258877 | 3258877 | 3258877 | 3258877
|  |  | Total |  |  | 24349538 | 24962130.4 | 25549457 | 26162038.8 | 26749265.4
| Departmental charges @ 11.0 % |  |  |  |  | 2678449.18 | 2745834.344 | 2810440.27 | 2877824.268 | 2942419.194
|  |  | Grand Total |  |  | 27027987.18 | 27707964.744 | 28359897.27 | 29039863.068 | 29691684.594
|  |  | Say Rs. In lacs :- |  |  | 270.2799 | 277.0796 | 283.599 | 290.3986 | 296.9168
PAGE-9
Cost of Terminal Equipments for 2x'X' MVA, 33/11 kV Sub-Station (Manned) with 4 to 8 nos. out going Feeders incorporating
Common Breaker ( vacuum/SF6 ) Control for Transformer (excluding cost of power Transformer and 11 kV incoming cables )
S.No. | Description of item | ISS.No. | Unit | Qty | Rate | Amount for Sub-Station With No. of out going Feeders.
|  | REC Std. No |  |  | Rs. | 4 Nos. | 5 Nos. | 6 Nos. | 7 Nos. | 8 Nos.
A) | Sub-Station Transformer
| 100 kVA, 33/0.4 kV S/Stn, Transformer |  | No. | 1 | 302741 | 302741 | 302741 | 302741 | 302741 | 302741
B) | 33 kV Switchgear Equipment
1 | 33 kV T/F C&R Panel without Differential Relay |  | No. | 2 | 225756 | 451512 | 451512 | 451512 | 451512 | 451512
2 | 33 kV Bus Coupler Panel |  | No. | 1 | 207654 | 207654 | 207654 | 207654 | 207654 | 207654
3 | 33 kV Feeder Panel |  | No. | 2 | 267870 | 535740 | 535740 | 535740 | 535740 | 535740
4 | 33 kV CT's Single Unit | 2705/1992 | No. | 6 | 30926 | 185556 | 185556 | 185556 | 185556 | 185556
5 | 33/11 kV, single phase PT's | 3156/1992 | No. | 3 | 26809 | 80427 | 80427 | 80427 | 80427 | 80427
6 | 33 kV Isolator with E/Blade | 9921/1992 | No. | 1 | 77702 | 77702 | 77702 | 77702 | 77702 | 77702
7 | 33 kV Isolator without E/Blade | 9921/1992 | No. | 7 | 71339 | 499373 | 499373 | 499373 | 499373 | 499373
8 | 33 kV lightening arresters metal oxide type | 55/1987 | set | 5 | 5359 | 26795 | 26795 | 26795 | 26795 | 26795
9 | 33 kV Expulsion Dropout fuse unit | 5292/1970 | set | 2 | 9614 | 19228 | 19228 | 19228 | 19228 | 19228
| S/Total (B) :- |  |  |  |  | 2083987 | 2083987 | 2083987 | 2083987 | 2083987
C) | 11 kV switchgear and allied Equipment
(I) | 11 kV panel board with 2 incomer panels with PT's 1
busbar coupler and following of out going Feeder panels.
1 | 4 nos. set of 7 panels |  | set | 1 | 2336712 | 2336712 | -- | -- | -- | --
2 | 5 nos. set of 8 panels |  | set | 1 | 2670528 | -- | 2670528 | -- | -- | --
3 | 6 nos. set of 9 panels |  | set | 1 | 3004344 | -- | -- | 3004344 | -- | --
4 | 7 nos. set of 10 panels |  | set | 1 | 3338160 | -- | -- | -- | 3338160 | --
5 | 8 nos. set of 11 panels |  | set | 1 | 3671976 | -- | -- | -- | -- | 3671976
(II) | 11 kV triple pole GO Switch/Isolator without E/blade for S/Stn with
| following no. of out going Feeder | 1326/1977
1 | 4 nos. |  | set | 4 | 4430 | 17720 | -- | -- | -- | --
2 | 5 nos. |  | set | 5 | 4430 | -- | 22150 | -- | -- | --
3 | 6 nos. |  | set | 6 | 4430 | -- | -- | 26580 | -- | --
4 | 7 nos. |  | set | 7 | 4430 | -- | -- | -- | 31010 | --
5 | 8 nos. |  | set | 8 | 4430 | -- | -- | -- | -- | 35440
PAGE-10
(III) | 11 kV LA's Sub-Station Type for S/Stn with
following no. of out going Feeder
1 | 4 nos. |  | No. | 12 | 345 | 4140 | -- | -- | -- | --
2 | 5 nos. |  | No. | 15 | 345 | -- | 5175 | -- | -- | --
3 | 6 nos. |  | No. | 18 | 345 | -- | -- | 6210 | -- | --
4 | 7 nos. |  | No. | 21 | 345 | -- | -- | -- | 7245 | --
5 | 8 nos. |  | No. | 24 | 345 | -- | -- | -- | -- | 8280
(IV) | 95 mm2, 11kV grade cable for S/Stn with
following no. of out going Feeder
1 | 4 nos. |  | mtr. | 200 | 697 | 139400 | -- | -- | -- | --
2 | 5 nos. |  | mtr. | 250 | 697 | -- | 174250 | -- | -- | --
3 | 6 nos. |  | mtr. | 300 | 697 | -- | -- | 209100 | -- | --
4 | 7 nos. |  | mtr. | 350 | 697 | -- | -- | -- | 243950 | --
5 | 8 nos. |  | mtr. | 400 | 697 | -- | -- | -- | -- | 278800
(V) | 11 kV epoxy terminating kits for S/Stn with
following no. of out going Feeder
1 | 4 nos. |  | No. | 4 | 7927 | 31708 | -- | -- | -- | --
2 | 5 nos. |  | No. | 5 | 7927 | -- | 39635 | -- | -- | --
3 | 6 nos. |  | No. | 6 | 7927 | -- | -- | 47562 | -- | --
4 | 7 nos. |  | No. | 7 | 7927 | -- | -- | -- | 55489 | --
5 | 8 nos. |  | No. | 8 | 7927 | -- | -- | -- | -- | 63416
(VI) | HT compound & other material in sets for cable boxes
of panels,S/Stn with following no. of out going Feeder
1 | 4 nos. |  | No. | 4 | 2179 | 8716 | -- | -- | -- | --
2 | 5 nos. |  | No. | 5 | 2179 | -- | 10895 | -- | -- | --
3 | 6 nos. |  | No. | 6 | 2179 | -- | -- | 13074 | -- | --
4 | 7 nos. |  | No. | 7 | 2179 | -- | -- | -- | 15253 | --
5 | 8 nos. |  | No. | 8 | 2179 | -- | -- | -- | -- | 17432
| S/Total (C) :- |  |  |  |  | 2538396 | 2922633 | 3306870 | 3691107 | 4075344
D) | General Equipment
1 | 30 V, 100 AH-Ni-Cd battery alongwith Battery charger | 34/1984 | No. | 1 | 113790 | 113790 | 113790 | 113790 | 113790 | 113790
2 | 400 V, A.C. distribution switchgear | 4047/1967 | No. | 1 | 514640 | 514640 | 514640 | 514640 | 514640 | 514640
| S/Total (D) :- |  |  |  |  | 628430 | 628430 | 628430 | 628430 | 628430
PAGE-11
E) | Super structure & busbar
(I) | 33 kV super structure & busbar as per detail (P-33) |  | job | 1 | 569160 | 569160 | 569160 | 569160 | 569160 | 569160
(II) | 11 kV super structure & busbar detail as per for Sub-Station
with following no. of out going Feeder (P-36)
1 | 4 nos. |  | job | 1 | 162440 | 162440 | -- | -- | -- | --
2 | 5 nos. |  | job | 1 | 220740 | -- | 220740 | -- | -- | --
3 | 6 nos. |  | job | 1 | 255110 | -- | -- | 255110 | -- | --
4 | 7 nos. |  | job | 1 | 313410 | -- | -- | -- | 313410 | --
5 | 8 nos. |  | job | 1 | 347780 | -- | -- | -- | -- | 347780
| S/Total (E) :- |  |  |  |  | 731600 | 789900 | 824270 | 882570 | 916940
F | Earthing of 33 kV Sub-Station Equipments as per detail (P-38) |  | job | 1 | 227620 | 227620 | 227620 | 227620 | 227620 | 227620
G | Yard & colony fencing as per detail (P-43) |  | job | 1 | 388930 | 388930 | 388930 | 388930 | 388930 | 388930
H | Yard lightening as per detail (P-44) |  | job | 1 | 117590 | 117590 | 117590 | 117590 | 117590 | 117590
I | Control and LT power cables as per detail (P-45) |  | job | 1 | 75160 | 75160 | 75160 | 75160 | 75160 | 75160
J) | Foundation of :--
1 | Transformer as per detail (P-46) |  | job | 2 | 38050 | 76100 | 76100 | 76100 | 76100 | 76100
K | Cost of trenches as per detail (P-50) |  | job | 1 | 299040 | 299040 | 299040 | 299040 | 299040 | 299040
| S/Total (F to K) :- |  |  |  |  | 1184440 | 1184440 | 1184440 | 1184440 | 1184440
| Grand Total (A to K ) :- |  |  |  |  | 7469594 | 7912131 | 8330738 | 8773275 | 9191882
| Say Rs. :- |  |  |  |  | 7469590 | 7912130 | 8330740 | 8773280 | 9191880
PAGE-12
Cost of Terminal Equipments for 1x'X' MVA, 33/11 kV Sub-Station ( Manned) with 4 to 8 nos. out going Feeder incorporating
independent Breaker ( vacuum/SF6 ) Control for Transformer (excluding cost of power Transformer and 11 kV incoming cables )
S.No. | Description of item | ISS.No. | Unit | Qty | Rate | Amount for Sub-Station With No. of out going Feeders.
|  | REC Std. No |  |  |  | 4 Nos. | 5 Nos. | 6 Nos. | 7 Nos. | 8 Nos.
A) | Sub-Station Transformer
| 100 kVA, 33/0.4 kV S/Stn, Transformer |  | No. | 1 | 302741 | 302741 | 302741 | 302741 | 302741 | 302741
B) | 33 kV Switchgear Equipment
1 | 33 kV T/F C&R Panel without Differential Relay |  | No. | 1 | 225756 | 225756 | 225756 | 225756 | 225756 | 225756
2 | 33 kV Feeder Panel |  | No. | 1 | 267870 | 267870 | 267870 | 267870 | 267870 | 267870
3 | 33 kV CT's Single Unit | 2705/1992 | No. | 3 | 30926 | 92778 | 92778 | 92778 | 92778 | 92778
4 | 33/11 kV, single phase PT's | 3156/1992 | No. | 3 | 26809 | 80427 | 80427 | 80427 | 80427 | 80427
5 | 400A 33 kV Isolator with E/Blade | 9921/1992 | No. | 1 | 77702 | 77702 | 77702 | 77702 | 77702 | 77702
6 | 400A 33 kV Isolator without E/Blade | 9921/1992 | No. | 4 | 71339 | 285356 | 285356 | 285356 | 285356 | 285356
7 | 33 kV lightening arresters metal oxide type | 55/1987 | set | 3 | 5359 | 16077 | 16077 | 16077 | 16077 | 16077
8 | 33 kV Expulsion Dropout fuse unit | 5292/1970 | set | 1 | 9614 | 9614 | 9614 | 9614 | 9614 | 9614
| S/Total (B) :- |  |  |  |  | 1055580 | 1055580 | 1055580 | 1055580 | 1055580
C) | 11 kV switchgear and allied Equipment
(I) | 11 kV panel board with 1 incomer panel with PT's
and following of out going Feeder panels.
1 | 4 nos. set of 5 panels |  | set | 1 | 2336712 | 2336712 | -- | -- | -- | --
2 | 5 nos. set of 6 panels |  | set | 1 | 2670528 | -- | 2670528 | -- | -- | --
3 | 6 nos. set of 7 panels |  | set | 1 | 3004344 | -- | -- | 3004344 | -- | --
4 | 7 nos. set of 8 panels |  | set | 1 | 3338160 | -- | -- | -- | 3338160 | --
5 | 8 nos. set of 9 panels |  | set | 1 | 3671976 | -- | -- | -- | -- | 3671976
(II) | 11 kV triple pole GO Switch/Isolator without E/blade for S/Stn with
| following no. of out going Feeder | 1326/1977
1 | 4 nos. |  | No. | 4 | 4430 | 17720 | -- | -- | -- | --
2 | 5 nos. |  | No. | 5 | 4430 | -- | 22150 | -- | -- | --
3 | 6 nos. |  | No. | 6 | 4430 | -- | -- | 26580 | -- | --
4 | 7 nos. |  | No. | 7 | 4430 | -- | -- | -- | 31010 | --
5 | 8 nos. |  | No. | 8 | 4430 | -- | -- | -- | -- | 35440
PAGE-13
(III) | 11 kV LA's Sub-Station Type for S/Stn with
following no. of out going Feeder
1 | 4 nos. |  | No. | 12 | 345 | 4140 | -- | -- | -- | --
2 | 5 nos. |  | No. | 15 | 345 | -- | 5175 | -- | -- | --
3 | 6 nos. |  | No. | 18 | 345 | -- | -- | 6210 | -- | --
4 | 7 nos. |  | No. | 21 | 345 | -- | -- | -- | 7245 | --
5 | 8 nos. |  | No. | 24 | 345 | -- | -- | -- | -- | 8280
(IV) | 95 mm2, 11kV grade cable for S/Stn with
| following no. of out going Feeder |  | mtr. | 200 | 697 | 139400 | -- | -- | -- | --
1 | 4 nos. |  | mtr. | 250 | 697 | -- | 174250 | -- | -- | --
2 | 5 nos. |  | mtr. | 300 | 697 | -- | -- | 209100 | -- | --
3 | 6 nos. |  | mtr. | 350 | 697 | -- | -- | -- | 243950 | --
4 | 7 nos. |  | mtr. | 400 | 697 | -- | -- | -- | -- | 278800
5 | 8 nos.
(V) | 11 kV epoxy terminating kits for S/Stn with
following no. of out going Feeder
1 | 4 nos. |  | No. | 4 | 7927 | 31708 | -- | -- | -- | --
2 | 5 nos. |  | No. | 5 | 7927 | -- | 39635 | -- | -- | --
3 | 6 nos. |  | No. | 6 | 7927 | -- | -- | 47562 | -- | --
4 | 7 nos. |  | No. | 7 | 7927 | -- | -- | -- | 55489 | --
5 | 8 nos. |  | No. | 8 | 7927 | -- | -- | -- | -- | 63416
(VI) | HT compound & other material in sets for cable boxes
of panels,S/Stn with following no. of out going Feeder
1 | 4 nos. |  | No. | 4 | 2179 | 8716 | -- | -- | -- | --
2 | 5 nos. |  | No. | 5 | 2179 | -- | 10895 | -- | -- | --
3 | 6 nos. |  | No. | 6 | 2179 | -- | -- | 13074 | -- | --
4 | 7 nos. |  | No. | 7 | 2179 | -- | -- | -- | 15253 | --
5 | 8 nos. |  | No. | 8 | 2179 | -- | -- | -- | -- | 17432
| S/Total (C) :- |  |  |  |  | 2538396 | 2922633 | 3306870 | 3691107 | 4075344
D) | General Equipment
1 | 30 V, 100 AH-Ni-Cd battery alongwith Battery charger | 34/1981 | No. | 1 | 113790 | 113790 | 113790 | 113790 | 113790 | 113790
2 | 400 V, A.C. distribution switchgear | 4047/1967 | No. | 1 | 514640 | 514640 | 514640 | 514640 | 514640 | 514640
| S/Total (D) :- |  |  |  |  | 628430 | 628430 | 628430 | 628430 | 628430
PAGE-14
E) | Super structure & busbar
I | 33 kV super structure & busbar as per detail (P-33) |  | job | 1 | 569160 | 569160 | 569160 | 569160 | 569160 | 569160
II | 11 kV super structure & busbar detail as per for Sub-Station
with following no. of out going Feeder (P-36)
1 | 4 nos. |  | job | 1 | 162440 | 162440 | -- | -- | -- | --
2 | 5 nos. |  | job | 1 | 220740 | -- | 220740 | -- | -- | --
3 | 6 nos. |  | job | 1 | 255110 | -- | -- | 255110 | -- | --
4 | 7 nos. |  | job | 1 | 313410 | -- | -- | -- | 313410 | --
5 | 8 nos. |  | job | 1 | 347780 | -- | -- | -- | -- | 347780
| S/Total (E) :- |  |  |  |  | 731600 | 789900 | 824270 | 882570 | 916940
F | Earthing of 33 kV Sub-Station Equipments as per detail (P-38) |  | job | 1 | 227620 | 227620 | 227620 | 227620 | 227620 | 227620
G | Yard & colony fencing as per detail (P-43) |  | job | 1 | 388930 | 388930 | 388930 | 388930 | 388930 | 388930
H | Yard lightening as per detail (P-44) |  | job | 1 | 117590 | 117590 | 117590 | 117590 | 117590 | 117590
I | Control and LT power cables as per detail (P-45) |  | job | 1 | 75160 | 75160 | 75160 | 75160 | 75160 | 75160
J) | Foundation of :--
1 | Transformer as per detail (P-46) |  | job | 1 | 38050 | 38050 | 38050 | 38050 | 38050 | 38050
K | Cost of trenches as per detail (P-50) |  | job | 1 | 299040 | 299040 | 299040 | 299040 | 299040 | 299040
| S/Total (F to K) :- |  |  |  |  | 1146390 | 1146390 | 1146390 | 1146390 | 1146390
| Grand Total (A to K ) :- |  |  |  |  | 6403137 | 6845674 | 7264281 | 7706818 | 8125425
| Say Rs. :- |  |  |  |  | 6403140 | 6845670 | 7264280 | 7706820 | 8125430
PAGE-15
Cost of Terminal Equipments for 2x'X' MVA, 33/11 kV Sub-station (Manned) with 4 to 8 nos. out going Feeders incorporating
independent Breaker ( vacuum/SF6 ) control for Transformer (excluding cost of power Transformer and 11 kV incoming cables )
S.No. | Description of item | ISS.No. | Unit | Qty | Rate | Amount for Sub-Station With No. of out going Feeders.
|  | REC Std. No |  |  | Rs. | 4 Nos. | 5 Nos. | 6 Nos. | 7 Nos. | 8 Nos.
A) | Sub-Station Transformer
| 100 kVA, 33/0.4 kV S/Stn, Transformer | 1180 & 2026 | No. | 1 | 302741 | 302741 | 302741 | 302741 | 302741 | 302741
B) | 33 kV Switchgear & Equipment
1 | 33 kV T/F C&R Panel with Differential Relay |  | No. | 2 | 432876 | 865752 | 865752 | 865752 | 865752 | 865752
2 | 33 kV Bus Coupler Panel |  | No. | 1 | 207654 | 207654 | 207654 | 207654 | 207654 | 207654
3 | 33 kV Feeder Panel |  | No. | 2 | 267870 | 535740 | 535740 | 535740 | 535740 | 535740
4 | 36 kV Vacuum/SF-6 Circuit Breaker. | 12-/1979 | No. | 2 | 253894 | 507788 | 507788 | 507788 | 507788 | 507788
5 | 33 kV CT's Single Unit | 2705/1992 | No. | 6 | 30926 | 185556 | 185556 | 185556 | 185556 | 185556
6 | 33/11 kV, single phase PT's | 3156/1992 | No. | 3 | 26809 | 80427 | 80427 | 80427 | 80427 | 80427
7 | 33 kV Isolator with E/Blade | 9921 | No. | 1 | 77702 | 77702 | 77702 | 77702 | 77702 | 77702
8 | 33 kV Expulsion Dropout fuse unit | 55/1987 | No. | 2 | 9614 | 19228 | 19228 | 19228 | 19228 | 19228
9 | 33 kV Isolator without E/Blade | 9921 | set | 7 | 71339 | 499373 | 499373 | 499373 | 499373 | 499373
10 | 33 kV lightening arresters metal oxide type | 5292/1970 | set | 5 | 5359 | 26795 | 26795 | 26795 | 26795 | 26795
| S/Total (B) :- |  |  |  |  | 3006015 | 3006015 | 3006015 | 3006015 | 3006015
C) | 11 kV switchgear and allied Equipment
I | 11 kV panel board with 2 incomer panels with PT's 1
busbar coupler and following out going Feeder panels.
1 | 4 nos. set of 7 panels |  | set | 1 | 2336712 | 2336712 | -- | -- | -- | --
2 | 5 nos. set of 8 panels |  | set | 1 | 2670528 | -- | 2670528 | -- | -- | --
3 | 6 nos. set of 9 panels |  | set | 1 | 3004344 | -- | -- | 3004344 | -- | --
4 | 7 nos. set of 10 panels |  | set | 1 | 3338160 | -- | -- | -- | 3338160 | --
5 | 8 nos. set of 11 panels |  | set | 1 | 3671976 | -- | -- | -- | -- | 3671976
II | 11 kV triple pole GO Switch/Isolator without E/blade for S/Stn with
| following no. of out going Feeder | 3070/1985
1 | 4 nos. |  | set | 4 | 4430 | 17720 | -- | -- | -- | --
2 | 5 nos. |  | set | 5 | 4430 | -- | 22150 | -- | -- | --
3 | 6 nos. |  | set | 6 | 4430 | -- | -- | 26580 | -- | --
4 | 7 nos. |  | set | 7 | 4430 | -- | -- | -- | 31010 | --
5 | 8 nos. |  | set | 8 | 4430 | -- | -- | -- | -- | 35440
PAGE-16
III | 11 kV LA's Sub-Station Type for S/Stn with
following no. of out going Feeder
1 | 4 nos. |  | No. | 12 | 345 | 4140 | -- | -- | -- | --
2 | 5 nos. |  | No. | 15 | 345 | -- | 5175 | -- | -- | --
3 | 6 nos. |  | No. | 18 | 345 | -- | -- | 6210 | -- | --
4 | 7 nos. |  | No. | 21 | 345 | -- | -- | -- | 7245 | --
5 | 8 nos. |  | No. | 24 | 345 | -- | -- | -- | -- | 8280
IV | 95 mm2, 11kV grade cable for S/Stn with
following no. of out going Feeder
1 | 4 nos. |  | mtr. | 200 | 697 | 139400 | -- | -- | -- | --
2 | 5 nos. |  | mtr. | 250 | 697 | -- | 174250 | -- | -- | --
3 | 6 nos. |  | mtr. | 300 | 697 | -- | -- | 209100 | -- | --
4 | 7 nos. |  | mtr. | 350 | 697 | -- | -- | -- | 243950 | --
5 | 8 nos. |  | mtr. | 400 | 697 | -- | -- | -- | -- | 278800
V | 11 kV epoxy terminating kits for S/Stn with
following no. of out going Feeder
1 | 4 nos. |  | No. | 4 | 7927 | 31708 | -- | -- | -- | --
2 | 5 nos. |  | No. | 5 | 7927 | -- | 39635 | -- | -- | --
3 | 6 nos. |  | No. | 6 | 7927 | -- | -- | 47562 | -- | --
4 | 7 nos. |  | No. | 7 | 7927 | -- | -- | -- | 55489 | --
5 | 8 nos. |  | No. | 8 | 7927 | -- | -- | -- | -- | 63416
VI | HT compound & other material in sets for cable boxes
of panels,S/Stn with following no. of out going Feeder
1 | 4 nos. |  | No. | 4 | 2179 | 8716 | -- | -- | -- | --
2 | 5 nos. |  | No. | 5 | 2179 | -- | 10895 | -- | -- | --
3 | 6 nos. |  | No. | 6 | 2179 | -- | -- | 13074 | -- | --
4 | 7 nos. |  | No. | 7 | 2179 | -- | -- | -- | 15253 | --
5 | 8 nos. |  | No. | 8 | 2179 | -- | -- | -- | -- | 17432
| S/Total (C) :- |  |  |  |  | 2538396 | 2922633 | 3306870 | 3691107 | 4075344
D) | General Equipment
1 | 30 V, 100 AH-Ni-Cd battery alongwith Battery charger | 34/1984 | No. | 1 | 113790 | 113790 | 113790 | 113790 | 113790 | 113790
| 400 V, A.C. distribution switchgear | 4047/1967 | No. | 1 | 514640 | 514640 | 514640 | 514640 | 514640 | 514640
| S/Total (D) :- |  |  |  |  | 628430 | 628430 | 628430 | 628430 | 628430
PAGE-17
E) | Super structure & busbar
I | 33 kV super structure & busbar as per detail (P-33) |  | job | 1 | 569160 | 569160 | 569160 | 569160 | 569160 | 569160
II | 11 kV super structure & busbar detail as per for Sub-Station
with following no. of out going Feeder (P-36)
1 | 4 nos. |  | job | 1 | 162440 | 162440 | -- | -- | -- | --
2 | 5 nos. |  | job | 1 | 220740 | -- | 220740 | -- | -- | --
3 | 6 nos. |  | job | 1 | 255110 | -- | -- | 255110 | -- | --
4 | 7 nos. |  | job | 1 | 313410 | -- | -- | -- | 313410 | --
5 | 8 nos. |  | job | 1 | 347780 | -- | -- | -- | -- | 347780
| S/Total (E) :- |  |  |  |  | 731600 | 789900 | 824270 | 882570 | 916940
F | Earthing of 33 kV Sub-Station Equipments as per detail (P-38) |  | job | 1 | 227620 | 227620 | 227620 | 227620 | 227620 | 227620
G | Yard & colony fencing as per detail (P-43) |  | job | 1 | 388930 | 388930 | 388930 | 388930 | 388930 | 388930
H | Yard lightening as per detail (P-44) |  | job | 1 | 117590 | 117590 | 117590 | 117590 | 117590 | 117590
I | Control and LT power cables as per detail (P-45) |  | job | 1 | 75160 | 75160 | 75160 | 75160 | 75160 | 75160
J) | Foundation of :--
1 | Transformer as per detail (P-46) |  | job | 2 | 38050 | 76100 | 76100 | 76100 | 76100 | 76100
2 | Circuit breaker (P-47) |  | job | 2 | 18330 | 36660 | 36660 | 36660 | 36660 | 36660
K | Cost of trenches as per detail (P-50) |  | job | 1 | 299040 | 299040 | 299040 | 299040 | 299040 | 299040
| S/Total (F to K) :- |  |  |  |  | 1221100 | 1221100 | 1221100 | 1221100 | 1221100
| Grand Total (A to K ) :- |  |  |  |  | 8428282 | 8870819 | 9289426 | 9731963 | 10150570
| Say Rs. :- |  |  |  |  | 8428280 | 8870820 | 9289430 | 9731960 | 10150570

## page 18-32
PAGE- 18
Cost of 2x 0.63 MVA, 33 kV Terminal Equipment & Sub-Station (Un-Manned) with 4 to 8 nos. of out going Feeders
with Common Breaker ( vacuum/SF6 ) Control for Transformer
S.No. | Description of item | ISS.No. | Unit | Qty | Rate | Amount for Sub-Station With No. of out going Feeders.
|  | REC Std. No |  |  | Rs. | 4 Nos. | 5 Nos. | 6 Nos. | 7 Nos. | 8 Nos.
1 | Cost of Terminal Equipments for 2x 0.63 MVA,33/11 kV Sub-Station |  | No. | 1 | -- | 8969170 | 9650480 | 10307870 | 10989190 | 11646580
with 4 to 8 nos. out going Feeder excluding the cost of Power Transformer
& 11 kV incoming cable (P- 24 to 26)
2 | 0.63 MVA, 33/11 kV Transformer | 2026/1993 | No. | 2 | 887500 | 1775000 | 1775000 | 1775000 | 1775000 | 1775000
3 | 95 mm2. 11 kV grade cable | 7098/1985 | Mtr | 100 | 697 | 69700 | 69700 | 69700 | 69700 | 69700
|  |  | S/Total |  |  | 10813870 | 11495180 | 12152570 | 12833890 | 13491280
| Storage Charges @ 3.0 % |  |  |  |  | 324416.1 | 344855.4 | 364577.1 | 385016.7 | 404738.4
| Contingencies Charges @ 3.0 % |  |  |  |  | 324416.1 | 344855.4 | 364577.1 | 385016.7 | 404738.4
| Transportation charges as per statement (P-61) |  |  |  |  | 312900 | 312900 | 312900 | 312900 | 312900
| Erection charges as per statement(P-74) |  |  |  |  | 3965200 | 4108700 | 4252200 | 4395800 | 4539300
| Cost of control room building as per detail(P-51) |  |  |  |  | 2727918 | 2727918 | 2727918 | 2727918 | 2727918
|  |  | Total |  |  | 18468720.2 | 19334408.8 | 20174742.2 | 21040541.4 | 21880874.8
| Departmental Charges @ 11.0 % |  |  |  |  | 2031559.222 | 2126784.968 | 2219221.642 | 2314459.554 | 2406896.228
|  |  | Grand Total |  |  | 20500279.422 | 21461193.768 | 22393963.842 | 23355000.954 | 24287771.028
|  |  | Say Rs. In lacs |  |  | 205.0028 | 214.6119 | 223.9396 | 233.55 | 242.8777
PAGE-19
Cost of 2x1.6 MVA, 33 kV Terminal Equipment & Sub-Station (Un-Manned) with 4 to 8 nos. of out going Feeders
with Common Breaker ( vacuum/SF6 ) Control for Transformer
S.No. | Description of item | ISS.No. | Unit | Qty | Rate | Amount for Sub-Station With No. of out going Feeders.
|  | REC Std. No |  |  | Rs. | 4 Nos. | 5 Nos. | 6 Nos. | 7 Nos. | 8 Nos.
1 | Cost of Terminal Equipments for 2x1.6 MVA,33/11 kV Sub-Station |  | No. | 1 | -- | 8969170 | 9650480 | 10307870 | 10989190 | 11646580
with 4 to 8 nos. out going Feeder excluding the cost of Power Transformer
& 11 kV incoming cable (P- 24 to 26)
2 | 1.6 MVA, 33/11 kV Transformer | 2026/1993 | No. | 2 | 1963500 | 3927000 | 3927000 | 3927000 | 3927000 | 3927000
3 | 120 mm2. 11 kV grade cable | 7098/1985 | No. | 100 | 965 | 96500 | 96500 | 96500 | 96500 | 96500
|  |  | S/Total |  |  | 12992670 | 13673980 | 14331370 | 15012690 | 15670080
| Storage Charges @ 3.0 % |  |  |  |  | 389780 | 410219 | 429941 | 450381 | 470102
| Contingencies Charges @ 3.0 % |  |  |  |  | 389780 | 410219 | 429941 | 450381 | 470102
| Transportation charges as per statement (P-61) |  |  |  |  | 312900 | 312900 | 312900 | 312900 | 312900
| Erection charges as per statement(P-74) |  |  |  |  | 3965200 | 4108700 | 4252200 | 4395800 | 4539300
| Cost of control room building as per detail(P-51) |  |  |  |  | 2727918 | 2727918 | 2727918 | 2727918 | 2727918
|  |  | Total |  |  | 20778248 | 21643936 | 22484270 | 23350070 | 24190402
| Departmental Charges @ 11.0 % |  |  |  |  | 2285607.28 | 2380832.96 | 2473269.7 | 2568507.7 | 2660944.22
|  |  | Grand Total |  |  | 23063855.28 | 24024768.96 | 24957539.7 | 25918577.7 | 26851346.22
|  |  | Say Rs. In lacs |  |  | 230.6386 | 240.2477 | 249.5754 | 259.1858 | 268.5135
PAGE-20
Cost of 1x1.6 MVA, Terminal Equipment & Sub-Station (Un-Manned) with 4 to 8 nos. out going Feeders
with Independent Breaker ( vacuum/SF6 ) Control for Transformer
S.No. | Description of item | ISS.No. | Unit | Qty | Rate | Amount for Sub-Station With No. of out going Feeders.
|  | REC Std. No |  |  |  | 4 Nos. | 5 Nos. | 6 Nos. | 7 Nos. | 8 Nos.
1 | Cost of Terminal Equipments for 1x1.6 MVA,33/11 kV Sub-Station |  | No. | 1 |  | 7630490 | 8311800 | 8969190 | 9650510 | 10307900
with 4 to 8 nos. out going Feeder excluding the cost of Power Transformer
& 11 kV incoming cable (P- 27 to 29)
2 | 1.6 MVA, 33/11 kV Transformer | 2026/1993 | No. | 1 | 1963500 | 1963500 | 1963500 | 1963500 | 1963500 | 1963500
3 | 120 mm2. 11 kV grade cable | 7098/1985 | No. | 50 | 965 | 48250 | 48250 | 48250 | 48250 | 48250
|  |  | S/Total |  |  | 9642240 | 10323550 | 10980940 | 11662260 | 12319650
| Storage Charges @ 3.0 % |  |  |  |  | 289267.2 | 309706.5 | 329428.2 | 349867.8 | 369589.5
| Contingencies Charges @ 3.0 % |  |  |  |  | 289267.2 | 309706.5 | 329428.2 | 349867.8 | 369589.5
| Transportation charges as per statement (P-61) |  |  |  |  | 312900 | 312900 | 312900 | 312900 | 312900
| Erection charges as per statement(P-74) |  |  |  |  | 3980100 | 4123600 | 4267200 | 4410700 | 4554200
| Cost of control room building as per detail(P-51) |  |  |  |  | 2727918 | 2727918 | 2727918 | 2727918 | 2727918
|  |  | Total |  |  | 17241692 | 18107381 | 18947814 | 19813514 | 20653847
| Departmental Charges @ 11.0 % |  |  |  |  | 1896586.12 | 1991811.91 | 2084259.54 | 2179486.54 | 2271923.17
|  |  | Grand Total |  |  | 19138278.12 | 20099192.91 | 21032073.54 | 21993000.54 | 22925770.17
|  |  | Say Rs. In lacs |  |  | 191.3828 | 200.9919 | 210.3207 | 219.93 | 229.2577
PAGE-21
Cost of 2x3.15 MVA, 33 kV Terminal Equipment & Sub-Station (Un-Manned) with 4 to 8 nos. out going Feeders
with Common Breaker ( vacuum/SF6 ) Control for Transformer
S.No. | Description of item | ISS.No. | Unit | Qty | Rate | Amount for Sub-Station With No. of out going Feeders.
|  | REC Std. No |  |  | Rs. | 4 Nos. | 5 Nos. | 6 Nos. | 7 Nos. | 8 Nos.
1 | Cost of Terminal Equipments for 2x 3.15 MVA,33/11 kV Sub-Station |  | No. | 1 | -- | 8969170 | 9650480 | 10307870 | 10989190 | 11646580
with 4 to 8 nos. out going Feeder excluding the cost of Power Transformer
&11 kV incoming cable (P- 24 to 26)
2 | 3.15 MVA, 33/11 kV Transformer | 2026/1992 | No. | 2 | 2472007 | 4944014 | 4944014 | 4944014 | 4944014 | 4944014
3 | 185 mm2. 11 kV grade cable | 7098/1985 | Mtr | 100 | 965 | 96500 | 96500 | 96500 | 96500 | 96500
|  |  | S/Total |  |  | 14009684 | 14690994 | 15348384 | 16029704 | 16687094
| Storage Charges @ 3.0 % |  |  |  |  | 420290.52 | 440729.82 | 460451.52 | 480891.12 | 500612.82
| Contingencies Charges @ 3.0 % |  |  |  |  | 420290.52 | 440729.82 | 460451.52 | 480891.12 | 500612.82
| Transportation charges as per statement (P-61) |  |  |  |  | 312900 | 312900 | 312900 | 312900 | 312900
| Erection charges as per statement(P-74) |  |  |  |  | 3965200 | 4108700 | 4252200 | 4395800 | 4539300
| Cost of control room building as per detail(P-51) |  |  |  |  | 2727918 | 2727918 | 2727918 | 2727918 | 2727918
|  |  | Total |  |  | 21856283.04 | 22721971.64 | 23562305.04 | 24428104.24 | 25268437.64
| Departmental Charges @ 11.0 % |  |  |  |  | 2404191.1344 | 2499416.8804 | 2591853.5544 | 2687091.4664 | 2779528.1404
|  |  | Grand Total |  |  | 24260474.1744 | 25221388.5204 | 26154158.5944 | 27115195.7064 | 28047965.7804
|  |  | Say Rs. In lacs |  |  | 242.6047 | 252.2139 | 261.5416 | 271.152 | 280.4797
PAGE-22
Cost of 1x3.15 MVA, Terminal Equipment & Sub-Station (Un-Manned) with 4 to 8 nos. out going Feeders
with Independent Breaker ( vacuum/SF6 ) Control for Transformer
S.No. | Description of item | ISS.No. | Unit | Qty | Rate | Amount for Sub-Station With No. of out going Feeders.
|  | REC Std. No |  |  |  | 4 Nos. | 5 Nos. | 6 Nos. | 7 Nos. | 8 Nos.
1 | Cost of Terminal Equipments for 1x3.15MVA,33/11 kV Sub-Station |  | No. | 1 | -- | 7630490 | 8311800 | 8969190 | 9650510 | 10307900
with 4 to 8 nos. out going Feeder excluding the cost of Power Transformer
& 11 kV incoming cable (P- 27 to 29)
2 | 3.15 MVA, 33/11 kV Transformer | 2026/1993 | No. | 1 | 2472007 | 2472007 | 2472007 | 2472007 | 2472007 | 2472007
3 | 185 mm2. 11 kV grade cable | 7098/1985 | No. | 50 | 965 | 48250 | 48250 | 48250 | 48250 | 48250
|  |  | S/Total |  |  | 10150747 | 10832057 | 11489447 | 12170767 | 12828157
| Storage Charges @ 3.0 % |  |  |  |  | 304522.41 | 324961.71 | 344683.41 | 365123.01 | 384844.71
| Contingencies Charges @ 3.0 % |  |  |  |  | 304522.41 | 324961.71 | 344683.41 | 365123.01 | 384844.71
| Transportation charges as per statement (P-61) |  |  |  |  | 312900 | 312900 | 312900 | 312900 | 312900
| Erection charges as per statement(P-74) |  |  |  |  | 3980100 | 4123600 | 4267200 | 4410700 | 4554200
| Cost of control room building as per detail(P-51) |  |  |  |  | 2727918 | 2727918 | 2727918 | 2727918 | 2727918
|  |  | Total |  |  | 17780710 | 18646398 | 19486832 | 20352531 | 21192864
| Departmental Charges @ 11.0 % |  |  |  |  | 1955878.1 | 2051103.78 | 2143551.52 | 2238778.41 | 2331215.04
|  |  | Grand Total |  |  | 19736588.1 | 20697501.78 | 21630383.52 | 22591309.41 | 23524079.04
|  |  | Say Rs. In lacs |  |  | 197.3659 | 206.975 | 216.3038 | 225.9131 | 235.2408
PAGE-23
Cost of 2x6.3 MVA, 33 kV Terminal Equipment & Sub-Station ( Un-Manned) with 4 to 8 nos. out going Feeders and
incorporating independent breaker ( vacuum/SF6 ) control for Transformer
S.No. | Description of item | ISS.No. | Unit | Qty | Rate | Amount for Sub-Station With No. of out going Feeders.
|  | REC Std. No |  |  | Rs. | 4 Nos. | 5 Nos. | 6 Nos. | 7 Nos. | 8 Nos.
1 | Cost of Terminal Equipments for 2x 6.3MVA,33/11 kV Sub-Station |  | No. | 1 | -- | 9383410 | 10064720 | 10722110 | 11403430 | 12060820
with 4 to 8 nos. out going Feeder excluding the cost of Power Transformer
& 11 kV incoming cable (P- 30 to 32)
2 | 6.3 MVA, 33/11 kV Transformer | 2026 | No. | 2 | 3642385 | 7284770 | 7284770 | 7284770 | 7284770 | 7284770
3 | 240 mm2. 11 kV grade cable | 7098/1985 | No. | 100 | 1338 | 133800 | 133800 | 133800 | 133800 | 133800
|  |  | S/Total |  |  | 16801980 | 17483290 | 18140680 | 18822000 | 19479390
| Storage Charges @ 3.0 % |  |  |  |  | 504059.4 | 524498.7 | 544220.4 | 564660 | 584381.7
| Contingencies Charges @ 3.0 % |  |  |  |  | 504059.4 | 524498.7 | 544220.4 | 564660 | 584381.7
| Transportation charges as per statement (P-61) |  |  |  |  | 312900 | 312900 | 312900 | 312900 | 312900
| Erection charges as per statement(P-74) |  |  |  |  | 3980100 | 4123600 | 4267200 | 4410700 | 4554200
| Cost of control room building as per detail(P-51) |  |  |  |  | 2727918 | 2727918 | 2727918 | 2727918 | 2727918
|  |  | Total |  |  | 24831016.8 | 25696705.4 | 26537138.8 | 27402838 | 28243171.4
| Departmental Charges @ 11.0 % |  |  |  |  | 2731411.848 | 2826637.594 | 2919085.268 | 3014312.18 | 3106748.854
|  |  | Grand Total |  |  | 27562428.648 | 28523342.994 | 29456224.068 | 30417150.18 | 31349920.254
|  |  | Say Rs. In lacs |  |  | 275.6243 | 285.2334 | 294.5622 | 304.1715 | 313.4992
PAGE-24
Cost of Terminal Equipments for 2x'X' MVA, 33/11 kV Sub-Station(Un-Manned) with 4 to 8 nos. out going Feeders incorporating
Common Breaker ( vacuum/SF6 ) Control for Transformer (excluding cost of power Transformer and 11 kV incoming cables )
S.No. | Description of item | ISS.No. | Unit | Qty | Rate | Amount for Sub-Station With No. of out going Feeders.
|  | REC Std. No |  |  | Rs. | 4 Nos. | 5 Nos. | 6 Nos. | 7 Nos. | 8 Nos.
A) | Sub-Station Transformer
| 100 kVA, 33/0.4 kV S/Stn, Transformer |  | No. | 1 | 302741 | 302741 | 302741 | 302741 | 302741 | 302741
B) | 33 kV Switchgear Equipment
1 | 36 kV Vacuum/SF-6 Circuit Breaker. | 12-/1979 | No. | 2 | 253894 | 507788 | 507788 | 507788 | 507788 | 507788
2 | 33 kV T/F C&R Panel without Differential Relay |  | No. | 2 | 225756 | 451512 | 451512 | 451512 | 451512 | 451512
3 | 33 kV Bus Coupler Panel |  | No. | 1 | 207654 | 207654 | 207654 | 207654 | 207654 | 207654
4 | 33 kV Feeder Panel |  | No. | 2 | 267870 | 535740 | 535740 | 535740 | 535740 | 535740
5 | 33 kV CT's Single Unit | 2705/1992 | No. | 6 | 30926 | 185556 | 185556 | 185556 | 185556 | 185556
6 | 33/11 kV, single phase PT's | 3156/1992 | No. | 3 | 26809 | 80427 | 80427 | 80427 | 80427 | 80427
7 | 400A 33 kV Isolator with E/Blade (Motorised) | 9921/1992 | No. | 1 | 77702 | 77702 | 77702 | 77702 | 77702 | 77702
8 | 400A 33 kV Isolator without E/Blade (Motorised) | 9921/1992 | No. | 7 | 71339 | 499373 | 499373 | 499373 | 499373 | 499373
9 | 33 kV lightening arresters metal oxide type | 55/1987 | set | 5 | 5359 | 26795 | 26795 | 26795 | 26795 | 26795
10 | 33 kV Expulsion Dropout fuse unit | 5292/1970 | set | 2 | 9614 | 19228 | 19228 | 19228 | 19228 | 19228
| S/Total (B) :- |  |  |  |  | 2591775 | 2591775 | 2591775 | 2591775 | 2591775
C) | 11 kV switchgear and allied Equipment
(I) | 11 kV panel board with 2 incomer panels with PT's 1
Busbar coupler and following of out going Feeder panels.
1 | 4 nos. set of 7 panels |  | set | 1 | 2336712 | 2336712 | -- | -- | -- | --
2 | 5 nos. set of 8 panels |  | set | 1 | 2670528 | -- | 2670528 | -- | -- | --
3 | 6 nos. set of 9 panels |  | set | 1 | 3004344 | -- | -- | 3004344 | -- | --
4 | 7 nos. set of 10 panels |  | set | 1 | 3338160 | -- | -- | -- | 3338160 | --
5 | 8 nos. set of 11 panels |  | set | 1 | 3671976 | -- | -- | -- | -- | 3671976
(II) | 11 kV triple pole GO Switch/Isolator without E/blade for S/Stn with
| following no. of out going Feeder | 1326/1977
1 | 4 nos. |  | set | 4 | 4430 | 17720 | -- | -- | -- | --
2 | 5 nos. |  | set | 5 | 4430 | -- | 22150 | -- | -- | --
3 | 6 nos. |  | set | 6 | 4430 | -- | -- | 26580 | -- | --
4 | 7 nos. |  | set | 7 | 4430 | -- | -- | -- | 31010 | --
5 | 8 nos. |  | set | 8 | 4430 | -- | -- | -- | -- | 35440
PAGE-25
(III) | 11 kV LA's Sub-Station Type for S/Stn with
following no. of out going Feeder
1 | 4 nos. |  | No. | 12 | 345 | 4140 | -- | -- | -- | --
2 | 5 nos. |  | No. | 15 | 345 | -- | 5175 | -- | -- | --
3 | 6 nos. |  | No. | 18 | 345 | -- | -- | 6210 | -- | --
4 | 7 nos. |  | No. | 21 | 345 | -- | -- | -- | 7245 | --
5 | 8 nos. |  | No. | 24 | 345 | -- | -- | -- | -- | 8280
(IV) | 95 mm2, 11kV grade cable for S/Stn with
following no. of out going Feeder
1 | 4 nos. |  | mtr. | 200 | 697 | 139400 | -- | -- | -- | --
2 | 5 nos. |  | mtr. | 250 | 697 | -- | 174250 | -- | -- | --
3 | 6 nos. |  | mtr. | 300 | 697 | -- | -- | 209100 | -- | --
4 | 7 nos. |  | mtr. | 350 | 697 | -- | -- | -- | 243950 | --
5 | 8 nos. |  | mtr. | 400 | 697 | -- | -- | -- | -- | 278800
(V) | 11 kV epoxy terminating kits for S/Stn with
following no. of out going Feeder
1 | 4 nos. |  | No. | 4 | 7927 | 31708 | -- | -- | -- | --
2 | 5 nos. |  | No. | 5 | 7927 | -- | 39635 | -- | -- | --
3 | 6 nos. |  | No. | 6 | 7927 | -- | -- | 47562 | -- | --
4 | 7 nos. |  | No. | 7 | 7927 | -- | -- | -- | 55489 | --
5 | 8 nos. |  | No. | 8 | 7927 | -- | -- | -- | -- | 63416
(VI) | HT compound & other material in sets for cable boxes
of panels,S/Stn with following no. of out going Feeder
1 | 4 nos. |  | No. | 4 | 2179 | 8716 | -- | -- | -- | --
2 | 5 nos. |  | No. | 5 | 2179 | -- | 10895 | -- | -- | --
3 | 6 nos. |  | No. | 6 | 2179 | -- | -- | 13074 | -- | --
4 | 7 nos. |  | No. | 7 | 2179 | -- | -- | -- | 15253 | --
5 | 8 nos. |  | No. | 8 | 2179 | -- | -- | -- | -- | 17432
(VII) | 12 KV vacuum/SF-6 Circuit Breaker.
1 | 4 nos. |  | No. | 4 | 238781.1565 | 955124.626 | -- | -- | -- | --
2 | 5 nos. |  | No. | 5 | 238781.1565 | -- | 1193905.7824 | -- | -- | --
3 | 6 nos. |  | No. | 6 | 238781.1565 | -- | -- | 1432686.9389 | -- | --
4 | 7 nos. |  | No. | 7 | 238781.1565 | -- | -- | -- | 1671468.0954 | --
5 | 8 nos. |  | No. | 8 | 238781.1565 | -- | -- | -- | -- | 1910249.2519
| S/Total (C) :- |  |  |  |  | 3493520.626 | 4116538.7824 | 4739556.9389 | 5362575.0954 | 5985593.2519
PAGE-26
D) | General Equipment
1 | 30 V, 100 AH-Ni-Cd battery alongwith Battery charger | 34/1984 | No. | 1 | 113790 | 113790 | 113790 | 113790 | 113790 | 113790
2 | 400 V, A.C. distribution switchgear | 4047/1967 | No. | 1 | 514640 | 514640 | 514640 | 514640 | 514640 | 514640
| S/Total (D) :- |  |  |  |  | 628430 | 628430 | 628430 | 628430 | 628430
E) | Super Structure & Busbar
(I) | 33 kV super structure & busbar as per detail (P-33) |  | job | 1 | 569160 | 569160 | 569160 | 569160 | 569160 | 569160
(II) | 11 kV super structure & busbar detail as per for Sub-Station
with following no. of out going Feeder (P-36)
1 | 4 nos. |  | job | 1 | 162440 | 162440 | -- | -- | -- | --
2 | 5 nos. |  | job | 1 | 220740 | -- | 220740 | -- | -- | --
3 | 6 nos. |  | job | 1 | 255110 | -- | -- | 255110 | -- | --
4 | 7 nos. |  | job | 1 | 313410 | -- | -- | -- | 313410 | --
5 | 8 nos. |  | job | 1 | 347780 | -- | -- | -- | -- | 347780
| S/Total (E) :- |  |  |  |  | 731600 | 789900 | 824270 | 882570 | 916940
F | Earthing of 33 kV Sub-Station Equipments as per detail (P-38) |  | job | 1 | 227620 | 227620 | 227620 | 227620 | 227620 | 227620
G | Yard & colony fencing as per detail (P-43) |  | job | 1 | 388930 | 388930 | 388930 | 388930 | 388930 | 388930
H | Yard lightening as per detail (P-44) |  | job | 1 | 117590 | 117590 | 117590 | 117590 | 117590 | 117590
I | Control and LT power cables as per detail (P-45) |  | job | 1 | 75160 | 75160 | 75160 | 75160 | 75160 | 75160
J) | Foundation of :--
1 | Transformer as per detail (P-46) |  | job | 2 | 38050 | 76100 | 76100 | 76100 | 76100 | 76100
2 | Circuit breaker (P-47) |  | job | 2 | 18330 | 36660 | 36660 | 36660 | 36660 | 36660
K | Cost of trenches as per detail (P-50) |  | job | 1 | 299040 | 299040 | 299040 | 299040 | 299040 | 299040
| S/Total (F to K) :- |  |  |  |  | 1221100 | 1221100 | 1221100 | 1221100 | 1221100
| Grand Total (A to K ) :- |  |  |  |  | 8969166.626 | 9650484.7824 | 10307872.9389 | 10989191.0954 | 11646579.2519
| Say Rs. :- |  |  |  |  | 8969170 | 9650480 | 10307870 | 10989190 | 11646580
PAGE-27
Cost of Terminal Equipments for 1x'X' MVA, 33/11 kV Sub-Station ( Un-Manned) with 4 to 8 nos. out going Feeder incorporating
independent Breaker ( vacuum/SF6 ) Control for Transformer (excluding cost of power Transformer and 11 kV incoming cables )
S.No. | Description of item | ISS.No. | Unit | Qty | Rate | Amount for Sub-Station With No. of out going Feeders.
|  | REC Std. No |  |  |  | 4 Nos. | 5 Nos. | 6 Nos. | 7 Nos. | 8 Nos.
A) | Sub-Station Transformer
| 100 kVA, 33/0.4 kV S/Stn, Transformer |  | No. | 1 | 302741 | 302741 | 302741 | 302741 | 302741 | 302741
B) | 33 kV Switchgear Equipment
1 | 36 kV Vacuum/SF-6 Circuit Breaker. | 12-/1979 | No. | 1 | 253894 | 253894 | 253894 | 253894 | 253894 | 253894
2 | 33 kV T/F C&R Panel without Differential Relay |  | No. | 1 | 225756 | 225756 | 225756 | 225756 | 225756 | 225756
3 | 33 kV Feeder Panel |  | No. | 1 | 267870 | 267870 | 267870 | 267870 | 267870 | 267870
4 | 33 kV CT's Single Unit | 2705/1992 | No. | 3 | 30926 | 92778 | 92778 | 92778 | 92778 | 92778
5 | 33/11 kV, single phase PT's | 3156/1992 | No. | 3 | 26809 | 80427 | 80427 | 80427 | 80427 | 80427
6 | 400A 33 kV Isolator with E/Blade (Motorised) | 9921/1992 | No. | 1 | 77702 | 77702 | 77702 | 77702 | 77702 | 77702
7 | 400A 33 kV Isolator without E/Blade (Motorised) | 9921/1992 | No. | 4 | 71339 | 285356 | 285356 | 285356 | 285356 | 285356
8 | 33 kV lightening arresters metal oxide type | 55/1987 | set | 3 | 5359 | 16077 | 16077 | 16077 | 16077 | 16077
9 | 33 kV Expulsion Dropout fuse unit | 5292/1970 | set | 1 | 9614 | 9614 | 9614 | 9614 | 9614 | 9614
| S/Total (B) :- |  |  |  |  | 1309474 | 1309474 | 1309474 | 1309474 | 1309474
C) | 11 kV switchgear and allied Equipment
(I) | 11 kV panel board with 1 incomer panel with PT's
and following of out going Feeder panels.
1 | 4 nos. set of 5 panels |  | set | 1 | 2336712 | 2336712 | -- | -- | -- | --
2 | 5 nos. set of 6 panels |  | set | 1 | 2670528 | -- | 2670528 | -- | -- | --
3 | 6 nos. set of 7 panels |  | set | 1 | 3004344 | -- | -- | 3004344 | -- | --
4 | 7 nos. set of 8 panels |  | set | 1 | 3338160 | -- | -- | -- | 3338160 | --
5 | 8 nos. set of 9 panels |  | set | 1 | 3671976 | -- | -- | -- | -- | 3671976
(II) | 11 kV triple pole GO Switch/Isolator without E/blade for S/Stn with
| following no. of out going Feeder | 1326/1977
1 | 4 nos. |  | No. | 4 | 4430 | 17720 | -- | -- | -- | --
2 | 5 nos. |  | No. | 5 | 4430 | -- | 22150 | -- | -- | --
3 | 6 nos. |  | No. | 6 | 4430 | -- | -- | 26580 | -- | --
4 | 7 nos. |  | No. | 7 | 4430 | -- | -- | -- | 31010 | --
5 | 8 nos. |  | No. | 8 | 4430 | -- | -- | -- | -- | 35440
PAGE-28
(III) | 11 kV LA's Sub-Station Type for S/Stn with
following no. of out going Feeder
1 | 4 nos. |  | No. | 12 | 345 | 4140 | -- | -- | -- | --
2 | 5 nos. |  | No. | 15 | 345 | -- | 5175 | -- | -- | --
3 | 6 nos. |  | No. | 18 | 345 | -- | -- | 6210 | -- | --
4 | 7 nos. |  | No. | 21 | 345 | -- | -- | -- | 7245 | --
5 | 8 nos. |  | No. | 24 | 345 | -- | -- | -- | -- | 8280
(IV) | 95 mm2, 11kV grade cable for S/Stn with
following no. of out going Feeder
1 | 4 nos. |  | mtr. | 200 | 697 | 139400 | -- | -- | -- | --
2 | 5 nos. |  | mtr. | 250 | 697 | -- | 174250 | -- | -- | --
3 | 6 nos. |  | mtr. | 300 | 697 | -- | -- | 209100 | -- | --
4 | 7 nos. |  | mtr. | 350 | 697 | -- | -- | -- | 243950 | --
5 | 8 nos. |  | mtr. | 400 | 697 | -- | -- | -- | -- | 278800
(V) | 11 kV epoxy terminating kits for S/Stn with
following no. of out going Feeder
1 | 4 nos. |  | No. | 4 | 7927 | 31708 | -- | -- | -- | --
2 | 5 nos. |  | No. | 5 | 7927 | -- | 39635 | -- | -- | --
3 | 6 nos. |  | No. | 6 | 7927 | -- | -- | 47562 | -- | --
4 | 7 nos. |  | No. | 7 | 7927 | -- | -- | -- | 55489 | --
5 | 8 nos. |  | No. | 8 | 7927 | -- | -- | -- | -- | 63416
(VI) | HT compound & other material in sets for cable boxes
of panels,S/Stn with following no. of out going Feeder
1 | 4 nos. |  | No. | 4 | 2179 | 8716 | -- | -- | -- | --
2 | 5 nos. |  | No. | 5 | 2179 | -- | 10895 | -- | -- | --
3 | 6 nos. |  | No. | 6 | 2179 | -- | -- | 13074 | -- | --
4 | 7 nos. |  | No. | 7 | 2179 | -- | -- | -- | 15253 | --
5 | 8 nos. |  | No. | 8 | 2179 | -- | -- | -- | -- | 17432
(VII) | 12 KV vacuum/SF-6 Circuit Breaker
1 | 4 nos. |  | No. | 4 | 238781.1565 | 955124.626 | -- | -- | -- | --
2 | 5 nos. |  | No. | 5 | 238781.1565 | -- | 1193905.7824 | -- | -- | --
3 | 6 nos. |  | No. | 6 | 238781.1565 | -- | -- | 1432686.9389 | -- | --
4 | 7 nos. |  | No. | 7 | 238781.1565 | -- | -- | -- | 1671468.0954 | --
5 | 8 nos. |  | No. | 8 | 238781.1565 | -- | -- | -- | -- | 1910249.2519
| S/Total (C) :- |  |  |  |  | 3493520.626 | 4116538.7824 | 4739556.9389 | 5362575.0954 | 5985593.2519
PAGE-29
D) | General Equipment
1 | 30 V, 100 AH-Ni-Cd battery alongwith Battery charger | 34/1984 | No. | 1 | 113790 | 113790 | 113790 | 113790 | 113790 | 113790
2 | 400 V, A.C. distribution switchgear | 4047/1967 | No. | 1 | 514640 | 514640 | 514640 | 514640 | 514640 | 514640
| S/Total (D) :- |  |  |  |  | 628430 | 628430 | 628430 | 628430 | 628430
E) | Super Structure & Busbar
I | 33 kV super structure & busbar as per detail (P-33) |  | job | 1 | 569160 | 569160 | 569160 | 569160 | 569160 | 569160
II | 11 kV super structure & busbar detail as per for Sub-Station
with following no. of out going Feeder (P-36)
1 | 4 nos. |  | job | 1 | 162440 | 162440 | -- | -- | -- | --
2 | 5 nos. |  | job | 1 | 220740 | -- | 220740 | -- | -- | --
3 | 6 nos. |  | job | 1 | 255110 | -- | -- | 255110 | -- | --
4 | 7 nos. |  | job | 1 | 313410 | -- | -- | -- | 313410 | --
5 | 8 nos. |  | job | 1 | 347780 | -- | -- | -- | -- | 347780
| S/Total (E) :- |  |  |  |  | 731600 | 789900 | 824270 | 882570 | 916940
F | Earthing of 33 kV Sub-Station Equipments as per detail (P-38) |  | job | 1 | 227620 | 227620 | 227620 | 227620 | 227620 | 227620
G | Yard & colony fencing as per detail (P-43) |  | job | 1 | 388930 | 388930 | 388930 | 388930 | 388930 | 388930
H | Yard lightening as per detail (P-44) |  | job | 1 | 117590 | 117590 | 117590 | 117590 | 117590 | 117590
I | Control and LT power cables as per detail (P-45) |  | job | 1 | 75160 | 75160 | 75160 | 75160 | 75160 | 75160
J) | Foundation of :--
1 | Transformer as per detail (P-46) |  | job | 1 | 38050 | 38050 | 38050 | 38050 | 38050 | 38050
2 | Circuit breaker (P-47) |  | job | 1 | 18330 | 18330 | 18330 | 18330 | 18330 | 18330
K | Cost of trenches as per detail (P-50) |  | job | 1 | 299040 | 299040 | 299040 | 299040 | 299040 | 299040
| S/Total (F to K) :- |  |  |  |  | 1164720 | 1164720 | 1164720 | 1164720 | 1164720
| Grand Total (A to K ) :- |  |  |  |  | 7630485.626 | 8311803.7824 | 8969191.9389 | 9650510.0954 | 10307898.2519
| Say Rs. :- |  |  |  |  | 7630490 | 8311800 | 8969190 | 9650510 | 10307900
PAGE-30
Cost of Terminal Equipments for 2x'X' MVA, 33/11 kV Sub-station (Un-Manned) with 4 to 8 nos. out going Feeders incorporating
independent Breaker ( vacuum/SF6 ) control for Transformer (excluding cost of power Transformer and 11 kV incoming cables )
S.No. | Description of item | ISS.No. | Unit | Qty | Rate | Amount for Sub-Station With No. of out going Feeders.
|  | REC Std. No |  |  | Rs. | 4 Nos. | 5 Nos. | 6 Nos. | 7 Nos. | 8 Nos.
A) | Sub-Station Transformer
| 100 kVA, 33/0.4 kV S/Stn, Transformer | 1180 & 2026 | No. | 1 | 302741 | 302741 | 302741 | 302741 | 302741 | 302741
B) | 33 kV Switchgear & Equipment
1 | 36 kV Vacuum/SF-6 Circuit Breaker. | 12-/1979 | No. | 2 | 253894 | 507788 | 507788 | 507788 | 507788 | 507788
2 | 33 kV T/F C&R Panel with Differential Relay |  | No. | 2 | 432876 | 865752 | 865752 | 865752 | 865752 | 865752
3 | 33 kV Bus Coupler Panel |  | No. | 1 | 207654 | 207654 | 207654 | 207654 | 207654 | 207654
4 | 33 kV Feeder Panel |  | No. | 2 | 267870 | 535740 | 535740 | 535740 | 535740 | 535740
5 | 33 kV CT's Single Unit | 2705/1992 | No. | 6 | 30926 | 185556 | 185556 | 185556 | 185556 | 185556
6 | 33/11 kV, single phase PT's | 3156/1992 | No. | 3 | 26809 | 80427 | 80427 | 80427 | 80427 | 80427
7 | 33 kV Isolator with E/Blade (Motorised) | 9921 | No. | 1 | 77702 | 77702 | 77702 | 77702 | 77702 | 77702
8 | 33 kV Expulsion Dropout fuse unit | 55/1987 | No. | 2 | 9614 | 19228 | 19228 | 19228 | 19228 | 19228
9 | 33 kV Isolator without E/Blade (Motorised) | 9921 | set | 7 | 71339 | 499373 | 499373 | 499373 | 499373 | 499373
10 | 33 kV lightening arresters metal oxide type | 5292/1970 | set | 5 | 5359 | 26795 | 26795 | 26795 | 26795 | 26795
| S/Total (B) :- |  |  |  |  | 3006015 | 3006015 | 3006015 | 3006015 | 3006015
C) | 11 kV switchgear and allied Equipment
I | 11 kV panel board with 2 incomer panels with PT's 1
Busbar coupler and following out going Feeder panels.
1 | 4 nos. set of 7 panels |  | set | 1 | 2336712 | 2336712 | -- | -- | -- | --
2 | 5 nos. set of 8 panels |  | set | 1 | 2670528 | -- | 2670528 | -- | -- | --
3 | 6 nos. set of 9 panels |  | set | 1 | 3004344 | -- | -- | 3004344 | -- | --
4 | 7 nos. set of 10 panels |  | set | 1 | 3338160 | -- | -- | -- | 3338160 | --
5 | 8 nos. set of 11 panels |  | set | 1 | 3671976 | -- | -- | -- | -- | 3671976
II | 11 kV triple pole GO Switch/Isolator without E/blade for S/Stn with
| following no. of out going Feeder | 3070/1985
1 | 4 nos. |  | set | 4 | 4430 | 17720 | -- | -- | -- | --
2 | 5 nos. |  | set | 5 | 4430 | -- | 22150 | -- | -- | --
3 | 6 nos. |  | set | 6 | 4430 | -- | -- | 26580 | -- | --
4 | 7 nos. |  | set | 7 | 4430 | -- | -- | -- | 31010 | --
5 | 8 nos. |  | set | 8 | 4430 | -- | -- | -- | -- | 35440
PAGE-31
III | 11 kV LA's Sub-Station Type for S/Stn with
following no. of out going Feeder
1 | 4 nos. |  | No. | 12 | 345 | 4140 | -- | -- | -- | --
2 | 5 nos. |  | No. | 15 | 345 | -- | 5175 | -- | -- | --
3 | 6 nos. |  | No. | 18 | 345 | -- | -- | 6210 | -- | --
4 | 7 nos. |  | No. | 21 | 345 | -- | -- | -- | 7245 | --
5 | 8 nos. |  | No. | 24 | 345 | -- | -- | -- | -- | 8280
IV | 95 mm2, 11kV grade cable for S/Stn with
following no. of out going Feeder
1 | 4 nos. |  | mtr. | 200 | 697 | 139400 | -- | -- | -- | --
2 | 5 nos. |  | mtr. | 250 | 697 | -- | 174250 | -- | -- | --
3 | 6 nos. |  | mtr. | 300 | 697 | -- | -- | 209100 | -- | --
4 | 7 nos. |  | mtr. | 350 | 697 | -- | -- | -- | 243950 | --
5 | 8 nos. |  | mtr. | 400 | 697 | -- | -- | -- | -- | 278800
V | 11 kV epoxy terminating kits for S/Stn with
following no. of out going Feeder
1 | 4 nos. |  | No. | 4 | 7927 | 31708 | -- | -- | -- | --
2 | 5 nos. |  | No. | 5 | 7927 | -- | 39635 | -- | -- | --
3 | 6 nos. |  | No. | 6 | 7927 | -- | -- | 47562 | -- | --
4 | 7 nos. |  | No. | 7 | 7927 | -- | -- | -- | 55489 | --
5 | 8 nos. |  | No. | 8 | 7927 | -- | -- | -- | -- | 63416
VI | HT compound & other material in sets for cable boxes
of panels,S/Stn with following no. of out going Feeder
1 | 4 nos. |  | No. | 4 | 2179 | 8716 | -- | -- | -- | --
2 | 5 nos. |  | No. | 5 | 2179 | -- | 10895 | -- | -- | --
3 | 6 nos. |  | No. | 6 | 2179 | -- | -- | 13074 | -- | --
4 | 7 nos. |  | No. | 7 | 2179 | -- | -- | -- | 15253 | --
5 | 8 nos. |  | No. | 8 | 2179 | -- | -- | -- | -- | 17432
(VII) | 12 KV vacuum/SF-6 Circuit Breaker.
1 | 4 nos. |  | No. | 4 | 238781.1565 | 955124.626 | -- | -- | -- | --
2 | 5 nos. |  | No. | 5 | 238781.1565 | -- | 1193905.7824 | -- | -- | --
3 | 6 nos. |  | No. | 6 | 238781.1565 | -- | -- | 1432686.9389 | -- | --
4 | 7 nos. |  | No. | 7 | 238781.1565 | -- | -- | -- | 1671468.0954 | --
5 | 8 nos. |  | No. | 8 | 238781.1565 | -- | -- | -- | -- | 1910249.2519
| S/Total (C) :- |  |  |  |  | 3493520.626 | 4116538.7824 | 4739556.9389 | 5362575.0954 | 5985593.2519
PAGE-32
D) | General Equipment
1 | 30 V, 100 AH-Ni-Cd battery alongwith Battery charger | 34/1984 | No. | 1 | 113790 | 113790 | 113790 | 113790 | 113790 | 113790
| 400 V, A.C. distribution switchgear |  | No. | 1 | 514640 | 514640 | 514640 | 514640 | 514640 | 514640
| S/Total (D) :- |  |  |  |  | 628430 | 628430 | 628430 | 628430 | 628430
E) | Super Structure & Busbar
I | 33 kV super structure & busbar as per detail (P-33) |  | job | 1 | 569160 | 569160 | 569160 | 569160 | 569160 | 569160
II | 11 kV super structure & busbar detail as per for Sub-Station
with following no. of out going Feeder (P-36)
1 | 4 nos. |  | job | 1 | 162440 | 162440 | -- | -- | -- | --
2 | 5 nos. |  | job | 1 | 220740 | -- | 220740 | -- | -- | --
3 | 6 nos. |  | job | 1 | 255110 | -- | -- | 255110 | -- | --
4 | 7 nos. |  | job | 1 | 313410 | -- | -- | -- | 313410 | --
5 | 8 nos. |  | job | 1 | 347780 | -- | -- | -- | -- | 347780
| S/Total (E) :- |  |  |  |  | 731600 | 789900 | 824270 | 882570 | 916940
F | Earthing of 33 kV Sub-Station Equipments as per detail (P-38) |  | job | 1 | 227620 | 227620 | 227620 | 227620 | 227620 | 227620
G | Yard & colony fencing as per detail (P-43) |  | job | 1 | 388930 | 388930 | 388930 | 388930 | 388930 | 388930
H | Yard lightening as per detail (P-44) |  | job | 1 | 117590 | 117590 | 117590 | 117590 | 117590 | 117590
I | Control and LT power cables as per detail (P-45) |  | job | 1 | 75160 | 75160 | 75160 | 75160 | 75160 | 75160
J) | Foundation of :--
1 | Transformer as per detail (P-46) |  | job | 2 | 38050 | 76100 | 76100 | 76100 | 76100 | 76100
2 | Circuit breaker (P-47) |  | job | 2 | 18330 | 36660 | 36660 | 36660 | 36660 | 36660
K | Cost of trenches as per detail (P-50) |  | job | 1 | 299040 | 299040 | 299040 | 299040 | 299040 | 299040
| S/Total (F to K) :- |  |  |  |  | 1221100 | 1221100 | 1221100 | 1221100 | 1221100
| Grand Total (A to K ) :- |  |  |  |  | 9383406.626 | 10064724.7824 | 10722112.9389 | 11403431.0954 | 12060819.2519
| Say Rs. :- |  |  |  |  | 9383410 | 10064720 | 10722110 | 11403430 | 12060820

## Page 34-37
PAGE-33
33 KV super structure and bus-bar for 33/11 kV or 33/22 KV S/Stn.
S.No. | Description of item | Unit | Qty | Rate (Rs.) | Amount(Rs.)
A. | SUPER STRUCTURE
1 | R.S. Joists, size 10,000x225x150mm 12 supports
| I.e. (12x10x33.9)=4068kg say 4.07 MT | MT | 4.07 | 50267 | 204586.69
2 | R.S.Joists, size 4200x225x150mm
supports for lightening arrester differential CT's
| (6x33.9x4.2) =854 kg say .854 MT | MT | 0.854 | 50267 | 42928.018
3 | Foundation of R.S. joists supports as per detail p-37 | job | 18 | 5520 | 99360
4 a) | M.S. channel iron 125x65mm, X-arm @13.1 kg/mtr. At
5% wastage for bus-bar,isolators,LA's,transformer etc.
I | 9150 mm long =9 no. I.e. 1098.14 kg
II | 4725 mm long =14 no. I.e. 882.11 kg
III | 750 mm long =2 no. I.e. 20.00 kg
| Total =25 no. I.e. 2000.25 kg =2 MT | MT | 2 | 50267 | 100534
b) | Add 5 % workshop charges on item 4 a) |  |  |  | 5026.7
5 a) | M.S. angle iron 65x65 X-arm @ 5.8 kg/mtr & 5% wastage for | MT | 0.067 | 50267 | 3367.889
body supports belt of station transformer
b) | Add 5% w/shop charge on item 5 a) |  |  |  | 168.3945
| Nuts & Bolts with Washers off sizes | Kg | 60 | 68 | 4080
| S/Total (A) :- |  |  |  | 460051.6915
B. | BUS-BAR
I | 3 disc insulators tension string complete with fitting p-54 | No. | 51 | 1643 | 83793
II | ACSR conductor 100 mm2 at 10 % wastage
| (8x4.5+1x3.5)x3x1.1=130.35 say 130 mtr. | mtr. | 130 | 55 | 7150
For jumpers at 2 mtr. average
| 25 sets I.e. 2x3x25x1.1=165 mtr. | mtr. | 165 | 55 | 9075
III | Tee connections | No. | 24 | 195 | 4680
IV | PG clamps | No. | 42 | 105 | 4410
| S/Total (B) :- |  |  |  | 109108
| Total (A+B) :- |  |  |  | 569159.6915
|  |  |  | Say Rs. | 569160
PAGE-34
11 kV Super Structure & Busbar for 33/11 kV Sub-Station.
S.No. | Description of item | Unit | Qty | Rate (Rs.) | Amount for out going Feeder of
|  |  |  | Rs | 4 no. | 5 no. | 6 no. | 7 no. | 8 no.
A | SUPPORTS
1 | Steel tubular pole 10 M long for:--
a | 4 nos. out going Feeder | No. | 4 | 11963 | 47852 | -- | -- | -- | --
b | 5 nos. out going Feeder | No. | 6 | 11963 | -- | 71778 | -- | -- | --
c | 6 nos. out going Feeder | No. | 6 | 11963 | -- | -- | 71778 | -- | --
d | 7 nos. out going Feeder | No. | 8 | 11963 | -- | -- | -- | 95704 | --
e | 8 nos. out going Feeder | No. | 8 | 11963 | -- | -- | -- | -- | 95704
2 | Steel tubular pole 9 M long for:--
a | 4 nos. out going Feeder | No. | 1 | 8174 | 8174 | -- | -- | -- | --
b | 5 nos. out going Feeder | No. | 1 | 8174 | -- | 8174 | -- | -- | --
c | 6 nos. out going Feeder | No. | 2 | 8174 | -- | -- | 16348 | -- | --
d | 7 nos. out going Feeder | No. | 2 | 8174 | -- | -- | -- | 16348 | --
e | 8 nos. out going Feeder | No. | 3 | 8174 | -- | -- | -- | -- | 24522
3 | RCC muffs & concreting thereof
a | 4 nos. out going Feeder | No. | 5 | 690 | 3450 | -- | -- | -- | --
b | 5 nos. out going Feeder | No. | 7 | 690 | -- | 4830 | -- | -- | --
c | 6 nos. out going Feeder | No. | 8 | 690 | -- | -- | 5520 | -- | --
d | 7 nos. out going Feeder | No. | 10 | 690 | -- | -- | -- | 6900 | --
e | 8 nos. out going Feeder | No. | 11 | 690 | -- | -- | -- | -- | 7590
| S/Total (A) :- |  |  |  | 59476 | 84782 | 93646 | 118952 | 127816
B | CROSS ARMS
1 | 3.75 long M.S. channel iron 100X50X6 mm
9.56kg/mtr. Cross arms for Sub-Station With
a | 4 nos. out going Feeder | No. | 30 | 1802 | 54060 | -- | -- | -- | --
b | 5 nos. out going Feeder | No. | 38 | 1802 | -- | 68476 | -- | -- | --
c | 6 nos. out going Feeder | No. | 46 | 1802 | -- | -- | 82892 | -- | --
d | 7 nos. out going Feeder | No. | 54 | 1802 | -- | -- | -- | 97308 | --
e | 8 nos. out going Feeder | No. | 62 | 1802 | -- | -- | -- | -- | 111724
PAGE-35
2 | 3.75 long M.S. angle iron 50X50X6 mm
4.5 kg/mtr. Cross arms for Sub-Station With
a | 4 nos. out going Feeder | No. | 16 | 848 | 13568 | -- | -- | -- | --
b | 5 nos. out going Feeder | No. | 20 | 848 | -- | 16960 | -- | -- | --
c | 6 nos. out going Feeder | No. | 24 | 848 | -- | -- | 20352 | -- | --
d | 7 nos. out going Feeder | No. | 28 | 848 | -- | -- | -- | 23744 | --
e | 8 nos. out going Feeder | No. | 32 | 848 | -- | -- | -- | -- | 27136
3 | M.S. half clamps with nuts & bolts for S/Stn with
a | 4 nos. out going Feeder | No. | 48 | 195 | 9360 | -- | -- | -- | --
b | 5 nos. out going Feeder | No. | 64 | 195 | -- | 12480 | -- | -- | --
c | 6 nos. out going Feeder | No. | 80 | 195 | -- | -- | 15600 | -- | --
d | 7 nos. out going Feeder | No. | 96 | 195 | -- | -- | -- | 18720 | --
e | 8 nos. out going Feeder | No. | 112 | 195 | -- | -- | -- | -- | 21840
| S/Total (B) :- |  |  |  | 76988 | 97916 | 118844 | 139772 | 160700
C 1. | BUS-BAR
Single insulators tension string for S/Stn with
a | 4 nos. out going Feeder | No. | 6 | 1039 | 6234 | -- | -- | -- | --
b | 5&6 nos. out going Feeder | No. | 12 | 1039 | -- | 12468 | 12468 | -- | --
c | 7&8 nos. out going Feeder | No. | 18 | 1039 | -- | -- | -- | 18702 | 18702
2 | ACSR CONDUCTOR
For bus-bars
a | 4 nos. out going Feeder | Mtr | 23 | 55 | 1265 | -- | -- | -- | --
b | 5&6 nos. out going Feeder | Mtr | 46 | 55 | -- | 2530 | 2530 | -- | --
c | 7&8 nos. out going Feeder | Mtr | 69 | 55 | -- | -- | -- | 3795 | 3795
For jumpers & 6 sets of jumpers at 2.5 mtr. Average
per Feeder for
a | 4 nos. out going Feeder | Mtr | 180 | 55 | 9900 | -- | -- | -- | --
b | 5 nos. out going Feeder | Mtr | 225 | 55 | -- | 12375 | -- | -- | --
c | 6 nos. out going Feeder | Mtr | 270 | 55 | -- | -- | 14850 | -- | --
d | 7 nos. out going Feeder | Mtr | 315 | 55 | -- | -- | -- | 17325 | --
e | 8 nos. out going Feeder | Mtr | 360 | 55 | -- | -- | -- | -- | 19800
PAGE-36
3 | 11 kV pin insulators with pin & helically formed fittings
a | 4 nos. out going Feeder | No. | 14 | 93 | 1302 | -- | -- | -- | --
b | 5 nos. out going Feeder | No. | 17 | 93 | -- | 1581 | -- | -- | --
c | 6 nos. out going Feeder | No. | 20 | 93 | -- | -- | 1860 | -- | --
d | 7 nos. out going Feeder | No. | 23 | 93 | -- | -- | -- | 2139 | --
e | 8 nos. out going Feeder | No. | 26 | 93 | -- | -- | -- | -- | 2418
4 | CLAMPS
a | 4 nos. out going Feeder | No. | 36 | 202 | 7272 | -- | -- | -- | --
b | 5 nos. out going Feeder | No. | 45 | 202 | -- | 9090 | -- | -- | --
c | 6 nos. out going Feeder | No. | 54 | 202 | -- | -- | 10908 | -- | --
d | 7 nos. out going Feeder | No. | 63 | 202 | -- | -- | -- | 12726 | --
e | 8 nos. out going Feeder | No. | 72 | 202 | -- | -- | -- | -- | 14544
| S/Total (C) :- |  |  |  | 25973 | 38044 | 42616 | 54687 | 59259
| Total (A+B+C):- |  |  |  | 162437 | 220742 | 255106 | 313411 | 347775
|  |  | Say Rs. |  | 162440 | 220740 | 255110 | 313410 | 347780
PAGE-37
Foundation of R.S. joists as per drawing no. HPSEB-154
S.No. | Description of item | Unit | Qty | Rate (Rs.) | Amount(Rs.)
1 i) | Round 12 mm dia =
0.925x2x4+0.625x2x4+0.4x2x4+1.927x4x3 =44.804 mtr
Adding 10 % wastage =49.28 mtr or 43.61 kg
ii) | Round 8 mm dia =
2x8x0.8+2x4x0.46+2x4x0.23+2x4x0.1 =17.52 mtr.
after adding 10% wastage =19.2 mtr. Or 7.52 kg
| Total (i+ii) = 51.13 say 52 kg | kg | 52 | 50 | 2600
2 i) | M.S. plate 225x160x10mm for top & bottom of R.S.
| joists supports I.e. 2x2.84 =5.68kg | kg | 5.68 | 50 | 284
ii) | Angle iron 50x50x6mm supports at the bottom of
| 2x0.15x4.5=1.35kg | kg | 1.35 | 50 | 67.5
3 | M.S. 16 mm dia foundation bolts with washers and nuts etc. | No. | 4 | 68 | 272
4 | R.C.C. 1:2:4=(1.155x0.96x0.08)+2(0.4x0.35x0.325)
.+2(0.35x0.208x0.205)+2(0.8x0.11x0.095)+2(1.72x0.205
x0.065)+2(0.517x0.05x0.045)=0.091+0.091+0.04+0.017
| .+0.046+0.002=0.287 | mtr. | 0.287 | 8002 | 2296.574
| Total :- |  |  |  | 5520.074
| Say Rs. |  |  |  | 5520

## page 38-52
PAGE-38
Schedule of cost for Earthing of 33/11 kV or 33/22 kV Sub-Station With indoor type of switchgear
S.No. | Description of item | Unit | Qty | Rate | Amount
Rs.
1 | Cost of material for earth mat laying as per detail P-40 | No | 1 | 189080 | 189080
2 | Earthing of 33 kV yard & equipment & 22 kV or 11kV
panels M.S. flat 20x60mm,wt. 1.2 kg/mtr. At 5% wastage
A. | For 3 no. Transformer earthing at 3 points (body & neutral) at
10 mtr. Each (3x3x10) 1.05=94.5 mtr.
B | For 3 sets of LA's at 20 mtr each 3x20x2x1.05=126 mtr.
C | For 4 nos. 33 kV super structure at 20 mtr each
4x2x20x1.05 =168 mtr.
D | For 2 nos. VCB & CT body earthing at 10 mtr. Each
(2x10)2x1.05
E | For earthing of 22 kV or 11kV super structure 80 mtr each
F | For earthing of 22 kV or 11kV super structure 15 mtr each
2x15x1.05 =31.5 mtr.
| Total (A+B+C+D+E+F) =542 mtr, 650 kg =0.65 MT | MT | 0.65 | 51536 | 33498.4
3 | Welding of risers and corrosion protection @ 5% of 2 |  |  |  | 1674.92
4 | GI wire no. 6 SWG for screening etc. | kg | 25 | 59 | 1475
5 | Eye block for screening | No | 30 | 63 | 1890
| Total :- |  |  |  | 227618.32
| Say Rs. |  |  |  | 227620
PAGE-39
Schedule of cost and material Earthing Electrode (pipe type) ( refer REC Construction Std. J-2 )
S.No. | Description of item | Unit | Qty | Rate | Amount
|  |  |  | Rs. | Rs.
1 | G.I. Pipe 50 mm dia with holes of 16 mm dia at 150 mm | No | 3 | 862 | 2586
from centre to centre for 2 mtr. Distance from bottom.
2 | Workshop charges 5 % on item no. 1 |  |  |  | 129.3
3 | M.S. plates 150x150x6mm for two connection | Kg | 1.13 | 50 | 56.5
4 | 50x6 mm M.S. flat connection with the mat to mat | Kg | 4.8 | 50 | 240
5 | Nuts & bolts galvanized 16 mm dia, 50 mm long | Kg | 0.5 | 68 | 34
6 | Chequred plate cover 500x500x6mm I.e. 11.8 kg | Kg | 11.8 | 75 | 885
| Total :- |  |  |  | 3930.8
| Say Rs. :- |  |  |  | 3930
PAGE-40
E 1.3 Schedule of cost & material for layout of Earthmat at 33/11 kV or 33/22 kV Sub-Station
S.No. | Description of item | Unit | Qty | Rate | Amount
|  |  |  | Rs. | Rs.
1 | M.S. flat 50x6 mm for ground mat including 5% wastage
& weighing 2.4 kg/mtr. 2(37x10+27x5)x1.05=1060.5 mtr.
| or 2545.2 kg say 2.55 MT | MT | 2.55 | 51536 | 131416.8
2 | Earthing pipe electrode as per detail No. E.1.2. | No. | 12 | 3930 | 47160
3 | 20 mm round, 3 mtr. Long & weighing 2.47 kg/mtr. 4 no.
| electrode 4x3x2.47 =29.64 kg, say 30 kg | Kg | 30 | 50 | 1500
4 | Welding etc. of points @ 5% on above items |  |  |  | 9003.84
| Total :- |  |  |  | 189080.64
| Say Rs. :- |  |  |  | 189080
PAGE-41
E 1.1 Extension Earthing of Equipments for 33 kV out going feeder
S.No. | Description of item | Unit | Qty | Rate | Amount
|  |  |  | Rs. | Rs.
1 | M.S. flat 20x6 mm weighting 1.2 kg/mtr at 10% wastage
a | For each set of LA's at 20 mtr each 20x2x1.1=44 mtr.
b | Structure at 20 mtr each 20x2x1.1= 44 mtr.
c | For 1 no. VCB & set of CT's body earthing at 10 mtr.
each 2x10x2x1.1 =44 mtr.
| Total a+b+c =132 mtr. Or 158 kg say 0.16 MT | MT | 0.16 | 51536 | 8245.76
d | Welding of riser and corrosion protection @ 5% of above |  |  |  | 412.288
2 | G.I. Wire no, 6 SWG for screening | kg | 10 | 59 | 590
3 | Eye block for screening | No. | 6 | 63 | 378
| Total :- |  |  |  | 9626.048
| Say Rs. :- |  |  |  | 9630
PAGE-42
Super structure for 33 kV bay for 1 no. out going feeder C.I.3(Extension) for each 33 kV VCB 33 kV
super structure and busbar controlled tapping for each outgoing 33kV feeder from existing 33 kV line
S.No. | Description of item | Unit | Qty | Rate | Amount
|  |  |  | Rs. | Rs.
A. | SUPER STRUCTURE
1 | R.S. Joists, size 10,000x225x150=746kg say 0.75 MT
| 37.3 kg/mt 2 no. supports I.e.(2x10x37.3) MT | MT | 0.75 | 50267 | 37700.25
2 | Foundation of R.S. joists supports as per detail P-37 | job | 2 | 5520 | 11040
3 a) | M.S. channel iron 125x65x6mm, X-arm @ 12.1 kg/mtr At
5% wastage for bus-bar,isolators,LA's,transformer etc.
I | 4650 mm long =7 no. I.e. 447.73 kg
II | 3725 mm long =2 no. I.e. 102.47 kg
| Total =9 no. I.e. 550.20 = 0.55 MT | MT | 0.55 | 50267 | 27646.85
b) | Add 5 % workshop charges on item 3 a) | MT |  |  | 1382.3425
4 | M.S. nuts and bolts (off size) with washers | Kg | 25 | 68 | 1700
| S/Total (A) :- |  |  |  | 79469.4425
B. | BUS-BAR
I | 3 disc insulators tension string complete with fitting P-54 | No. | 6 | 1643 | 9858
II | 3 disc suspension tension string complete with fitting P-54 | No. | 3 | 1553 | 4659
III | ACSR conductor 100 mm2 at 10 % wastage
a | for busbar
3.5x3x1.1 =11.55 mtr.
b | For jumpers at 2 mtr. average
9 sets I.e. 2x3x9x1.1=59.4 mtr.
| Total (a+b) =70.95 mtr. Say 71 mtr. | mtr. | 71 | 55 | 3905
c | PG clamps | No. | 21 | 105 | 2205
| S/Total (B) :- |  |  |  | 20627
| Total (A+B) :- |  |  |  | 100096.4425
| Say Rs. :- |  |  |  | 100100
PAGE-43
Schedule of cost & material for 33kV yard and colony fencing of 33/11 kV or 33/22 kV Sub-Station
S.No. | Description of item | Unit | Qty | Rate | Amount
|  |  |  | Rs. | Rs.
A) | Expended metal fencing around switchyard
1 | M.S. angle iron 65x65x6 mm, 3 M long supports 0.6 M
bent outwards at top & to contain 3 strands of barbed wire
0.4 mtr. Sagged and concreted in ground and 2 mtr.
Vertical for gauge fencing.
Supports required at every 2 mtr. For 127 mtr. Periphery
| of switchyard 64 nos. | No. | 64 | 1230.5239 | 78753.5309
2 | Expended metal at 10 % wastage 1.1x127x2=279.4 | Sq. mtr. | 280 | 836 | 234080
say 280 sq. mtr.
3 | G.I. Wire no. 6 SWG 6 strand all along the periphery to | MT | 0.126 | 58763 | 7404.138
hold the metal 10% wastage I.e. 1.1x127x6=833.2 M @
0.150 kg/mtr =125.73 kg or 0.126 MT
4 | Angle iron stays with eye hooks etc. for 20% of supports | set | 13 | 1243 | 5350
5 | Cement etc. for concreting of supports & angle iron stays | bag | 90 | 325 | 29250
6 | Barbed wire 3 strands of 127 mtr at 10% wastage | kg | 84 | 58 | 4872
1.1x3x127=419 mtr. =84 kg
| S/Total (A) |  |  |  | 359709.6689
B) | Gate at colony & switchyard entrance
a | Gate cost of masonry | No. | 3 | 1943 | 5829
b | M.S. angle iron 65x65x6 mm2 gates, 1.5x2.5 mtr. Each | Sq. mtr. | 7.5 | 729.2 | 5469
grill works 2 no. I.e. 2x1.5x2.5 = 7.5 sq.mtr.
c | Wicket gate | No. | 1 | 3311 | 3311
14609
| Cost of 2 no. gates :- |  |  |  | 29218
| Total (A+B) :- |  |  |  | 388927.6689
| Say Rs. |  |  |  | 388930
PAGE-44
Schedule of cost of yard lighting for 33/11 kV or 33/22 kV Sub-Station or 22 kV control point
S.No. | Description of item | Unit | Qty | Rate (Rs.) | Amount (Rs.)
1 | 8 mtr, 100 mm dia GI pipe poles for yard lighting | No. | 5 | 3840 | 19200
2 | Mercury vapour lamp fittings | No. | 17 | 3983 | 67711
3 | GI pipe bracket for murcury vapour lamp | No. | 17 | 428 | 7276
4 | Post Erection for gate | No. | 4 | 941 | 3764
5 | Clamps for GI pipe bracket | No. | 34 | 127 | 4318
6 | Underground cable 16 mm2 for yard lighting | Mtr | 220 | 64 | 14080
7 | PVC cable size 6 mm2 for connecting mercury vapour lamp supply | Mtr | 75 | 8 | 600
8 | Junction box | No. | 11 | 58 | 638
| Total :- |  |  |  | 117587
| Say Rs. |  |  |  | 117590
PAGE-45
I. 1.2 Schedule of cost and control cable for 33/11 kV or 33/22 kV Sub-Station using 22 kV indoor type switchgear.
(Refer P-53)
S.No. | Description of item | Unit | Length | Rate | Amount
|  |  |  | Rs. | Rs.
1 | 2x2.5 mm2 screened control cable | Mtr. | 605 | 35 | 21175
2 | 4x2.5 mm2 screened control cable | Mtr. | 300 | 63 | 18900
3 | 12x2.5 mm2 screened control cable | Mtr. | 125 | 161 | 20125
4 | 3.5 core 95 mm2 aluminium cable suitable for 415 V, AC | Mtr. | 55 | 272 | 14960
| Total :- |  |  |  | 75160
| Say Rs. |  |  |  | 75160
PAGE-46
Foundation of each of 33/11 kV or 33/22 kV Transformer (refer 33kV Sub-station standard layout)
S.No. | Description of item | Unit | Qty | Rate | Amount
|  |  |  | Rs. | Rs.
1 | PCC 1:4:8= 3.8X1.8X0.25=1.026 mm3 | m3 | 1.026 | 2452 | 2515.752
2 | RCC 1:2:4=(3.5X1.5X0.2)-2(1.4X0.325X0.175)-(1.4X0.39 | m3 | 0.837 | 8002 | 6697.674
X0.175)+2(0.68X0.35X0.175)=0.837
3 | M.S. round 12mm dia 230 mm center to center at 18% | kg | 73 | 50 | 3650
wastage (21x1.5+3.5x7x2)+(0.68x7x6x7x0.2)1.1=81.31
say 80 mtr. Or 72.9 kg, say 73 kg
4 | M.S. rails 133.8 kg/mtr. 2 no. 1.8 mtr. In length | kg | 402 | 50 | 20100
2x1.5x133.8=401.4 say 402 kg
5 | M.S angle iron slapper 75x75x8 mm, 2 nos. of 1.75 mtr | kg | 31.2 | 50 | 1560
length 1.75x2x8.9= 31.15 kg say 31.2 kg
6 | M.S. angle iron 65x65x6 mm supports along the M.S. | kg | 23.1 | 50 | 1155
rails 2x1.5x7.7=23.1 kg
7 | GI drain pipe 100 mm dia 2 mtr long | mtr | 2 | 899 | 1798
8 | Stoppers for Transformer wheels & horing of M.S. rails | L.S. |  |  | 572
& angle iron with stoppers.
| Total :- |  |  |  | 38048
| Say Rs. |  |  |  | 38050
PAGE-47
I.1.2 Foundation of each of 33 kV or 22 kV CB (outdoor type) - [33kV Sub-station Standard layout]
S.No. | Description of item | Unit | Qty | Rate | Amount
|  |  |  | Rs. | Rs.
1 | RCC 1:2:4 (2.3x1.75x0.05)+(2.2x1.65x0.5)=2.016 m3 | m3 | 2.016 | 8002 | 16132.032
2 | M.S. round 12 mm dia at 10% wastage | kg | 44 | 50 | 2200
1.1(10x1.65+8x2.2+5x4x0.6)=48.51 M =43.17 kg say 44
| Total :- |  |  |  | 18332
| Say Rs. |  |  |  | 18330
PAGE-48
Schedule of cost of construction of 1 mtr. of OB Type Trench with cover .
S.No. | Description of item | Unit | Qty | Rate | Amount
|  |  |  | Rs. | Rs.
1 | PCC 1:5:10=(1.13x0.075x1) =0.085 m3 | m3 | 0.085 | 2701 | 229.585
2 | PCC 1:2:4=( 0.075x0.25x1)+(0.025x0.25x1)+ | m3 | 0.021 | 4402 | 92.442
0.5(22/7x0.05x0.05)=0.021 m3
3 | RCC 1:2:4 =2(0.09x0.24x1)+(0.04x0.5x1)+ | m3 | 0.068 | 7052 | 479.536
0.043+0.025 =0.068
4 | Brick Masonary1:6=2(0.24x0.6x1)+(0.25x0.05x1)=0.301 m3 | m3 | 0.301 | 3607 | 1085.707
5 | 10 mm cement plaster in cement mortar | m2 | 0.085 | 75 | 6.375
1:4(22/7x0.05x1)+(0.25x1)=0.085 m2
6 | M.S. round 6 mm dia for at 10% wastage = | kg | 2.9 | 50 | 145
1.1(8x0.73+6x1) =13.02 mtr =2.9 kg
7 | Angle iron 40x40x6 mm at10% wastage= 0.49x3= | kg | 5.15 | 50 | 257.5
1.47 mtr. Or 5.15 kg
| Total :- |  |  |  | 2296.145
| Say Rs. |  |  |  | 2300
PAGE-49
Schedule of cost of construction of 1 mtr. of OC Type Trench with cover.
S.No. | Description of item | Unit | Qty | Rate | Amount
|  |  |  | Rs. | Rs.
1 | PCC 1:5:10=(0.98x0.075x1) =0.074 m3 | m3 | 0.074 | 2701 | 199.874
2 | PCC 1:2:4=2( 0.025x0.175x1)+0.5(0.05x0.175x1)=0.018 | m3 | 0.018 | 4402 | 79.236
3 | RCC 1:2:4 =2(0.09x0.24x1)+(0.05x0.35x1)= 0.061 | m3 | 0.061 | 8002 | 488.122
4 | Brick Masonry 1:6=2(0.24x0.21x1)=0.101 m3 | m3 | 0.101 | 3607 | 364.307
5 | 10 mm cement plaster in cement mortar 1:4= | m2 | 0.364 | 75 | 27.3
(0.152+0.152)x1=0.864 m2
6 | M.S. round 6 mm dia for at 10% wastage = | kg | 2.64 | 50 | 132
1.1(8x0.59+6x1) =11.792 mtr =2.64 kg
7 | Angle iron 40x40x6 mm, 8.3 mm long =2.01 kg | kg | 2.01 | 50 | 100.5
| Total :- |  |  |  | 1391.339
| Say Rs. |  |  |  | 1390
PAGE-50
Cost of Trenches in 33/11 kV or 33/22 kV Sub-Station
S.No. | Description of item | Unit | Length | Rate | Amount
|  |  |  | Rs. | Rs.
1 | Construction of OB type of Trench in the yard and | Mtr | 91.4 | 2300 | 210220
control room
2 | Construction of OC type of Trench in the yard and | Mtr | 63.9 | 1390 | 88821
control room
| Total :- |  |  |  | 299041
| Say Rs. |  |  |  | 299040
PAGE-51
Switch Room & Control Room Building of 33/11kV or 33/22 kV Sub-Station or 33 kV control point
S.No. | Description of item | Unit | Qty | Rate | Amount | Electrical installation & Water supply |  | Total
|  |  |  | Rs. | Rs. | service connection @5% | Storage tank@12.50% | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
A) | Manned Sub-Station
1 | Sub-Station Building/ Control Room of 120 sq. mtr Covered Area | Sq. mtr | 120 | 11297 | 1355640 | 67782 | 169455 | 1592877
2 | Cost of Land (tentative ) | Sq. mtr | 7000 | 238 | 1666000 |  |  | 1666000
| Total :- | [6 empty] | 3258877
B) | Un-Manned Sub-Station
1 | Sub-Station Building/ Control Room of 80 sq. mtr Covered Area | Sq. mtr | 80 | 11297 | 903760 | 45188 | 112970 | 1061918
2 | Cost of Land (tentative ) | Sq. mtr | 7000 | 238 | 1666000 |  |  | 1666000
| Total :- | [6 empty] | 2727918
PAGE-52
TERMINAL EQUIPMENT AND ALLIED MATERIAL FOR EACH OF 33 kV OUTGOING FEEDER
S.No. | Description of item | Iss.No. | Unit | Qty | Rate (Rs.) | Amount for 33/11 kV S/Stn. on which
|  | REC STD No. |  |  |  | PT already Installed | PT not installed
A) | 33 kV equipment
1 | 36 kV vacuum C.B. with control and relay panel | 12-/1979 | No. | 1 | 253894 | 253894 | 253894
2 | 33/11kV, single phase PT's | 3156 | No. | 3 | 26809 |  | 80427
3 | 33 kV multi core, multi ratio CT's | 2705 | set | 3 | 30926 | 92778 | 92778
4 | 33 kV isolator with E/Blade | 52/1964&1968 | set | 1 | 77702 | 77702 | 77702
5 | 33 kV isolator without E/Blade | 52/1987 | set | 2 | 71339 | 142678 | 142678
6 | 33 kV lightening arresters metal oxide type | 16/1981 | set | 1 | 5359 | 5359 | 5359
B | 33 kV super structure & busbar extension as per detail P-42 |  | job | 1 | 100100 | 100100 | 100100
C | Extension of earthing etc. as per detail P-41 |  | job | 1 | 9630 | 9630 | 9630
D | Foundation of circuit breaker as per detail P-47 |  | job | 1 | 18330 | 18330 | 18330
E | Additional control cables
| 4 core 2.5 mm2, 2x76 M |  | Mtr | 152 | 63 | 9576 | 9576
| 2 core 2.5 mm2, 2x76 M |  | Mtr | 76 | 35 | 2660 | 2660
| 12 core 2.5 mm2, 2x76 M |  | Mtr | 76 | 161 | 12236 | 12236
F | Trench O.B. type (additional ) as per detail P-48 |  | Mtr | 9 | 2300 | 20700 | 20700
|  | S/Total |  |  |  | 745643 | 826070
| Storage Charges @ 3.0 % |  |  |  |  | 22369.29 | 24782.1
| Contingencies Charges @ 3.0 % |  |  |  |  | 22369.29 | 24782.1
| Erection charges as per detail P-54 |  |  |  |  | 208790 | 216650
| Transportation charges as per statement P-63 |  |  |  |  | 32820 | 32820
|  | Total |  |  |  | 1031991.58 | 1125104.2
| Departmental Charges @ 11.0 % |  |  |  |  | 113519.0738 | 123761.462
|  | Grand Total |  |  |  | 1145510.6538 | 1248865.662
|  | Say Rs in lacs |  |  |  | 11.4551 | 12.4887

## Page-53
PAGE-53
I.1.1.(a) CONTROL CABLE SCHEDULE FOR 33/11 kV OR 33/22 kV S/STN. WITH COMMON BREAKER CONTROL
(Note this cable schedule is strictly for preparation of cost data, exact cable schedule be had as per site requirements from quarter concerned)
S.No. | Name of circuit | From | To | Purpose | Length in mtrs.
[5 empty] | 2x2.5 | 4x2.5 | 12x2.5 | 3.5x95
[5 empty] | mm2 | mm2 | mm2 | mm2
1 | 3-ph, 400 volt Stn. | Station | LT :AC Board | To carry supply from | -- | -- | -- | 50
| transformer supply | transformer |  | transformer to ctrl. room
2 | Indication circuit | I1 | 33 kV control panel | Carry isolator position indication | 70 | -- | -- | --
|  | I2 | 33 kV control panel | --do-- | 65 | -- | -- | --
|  | I2 | 33 kV control panel | --do-- | 56 | -- | -- | --
|  | I5 | 33 kV control panel | --do-- | 52 | -- | -- | --
|  | I6 | 33 kV control panel | --do-- | 47 | -- | -- | --
|  | I7 | 33 kV control panel | --do-- | 57 | -- | -- | --
|  | VCB | 33 kV control panel | To carry indication to carry | -- | 72 | -- | --
circuit healthy check
3 | AC circuit | VCB | AC control board | To change MOCB spring | -- | 72 | -- | --
|  | VCB | Control panel | Trip close | -- | 72 | -- | --
|  | VCB (CT's) | control Board | Metering, protection | -- | -- | 72 | --
|  | 33kV diff. CT's | control Board 33kV | Differential protection | -- | 55 | -- | --
|  | D.C. Board | control Board | Supply to the relay | -- | -- | 15 | --
|  | D.C. Board | 11/22kV control Board | --do-- | -- | -- | 25 | --
4 | Emergency lighting | D.C. Board | light points |  | 200 | -- | -- | --
|  |  |  | Sub-Total :- | 547 | 271 | 112 | 50
| 10% as wastage of above |  |  |  | 54.7 | 27.1 | 11.2 | 5
|  |  |  | Total :- | 601.7 | 298.1 | 123.2 | 55
|  |  |  | Say (Mtrs) | 605 | 300 | 125 | 55

## page-54
PAGE-54
Analysis for 1 disc insulator, 2 disc insulator, 3 disc insulator Tension/ Suspension, Strain Strings
S.No. | Description | unit | Qty | Rate ( Rs.) | Amount ( In Rs.)
[5 empty] | 1 disc insulator String |  | 2 disc insulator String |  | 3 disc insulator String
[5 empty] | Tension | Suspension | Tension | Suspension | Tension | Suspension
1 | Disc insulator 90 KN
I | For 1 disc insulator String | No. | 1 | 302 | 302 | 302 | -- | -- | -- | --
II | For 2 disc insulator String | No. | 2 | 302 | -- | -- | 604 | 604 | -- | --
III | For 3 disc insulator String | No. | 3 | 302 | -- | -- | -- | -- | 906 | 906
2 | Eye socket ball cleaves
I | For 1 disc insulator String | Set | 1 | 126 | 126 | 126 | -- | -- | -- | --
II | For 2 disc insulator String | Set | 1 | 126 | -- | -- | 126 | 126 | -- | --
III | For 3 disc insulator String | Set | 1 | 126 | -- | -- | -- | -- | 126 | 126
3 | Bend staple set/ chain link | No. | 1 | 166 | 166 | 166 | 166 | 166 | 166 | 166
4 | Dead end clamp for 65mm2 Cu-eq. Conductor | No. | 1 | 445 | 445 | -- | 445 | -- | 445 | --
5 | Suspension clamps for 65 mm2 Cu-eq. Conductor | No. | 1 | 355 | -- | 355 | -- | 355 | -- | 355
| Total :- |  |  |  | 1039 | 949 | 1341 | 1251 | 1643 | 1553

## page 54-60
PAGE-55
Cost of installation of 11 kV Auto Voltage Booster
S.No. | Description | Unit | Qty | Rate | Amount
|  |  |  | Rs. | Rs.
A) | EQUIPMENT
1 | 11 kV 1-Phase auto voltage booster outdoor type | No. | 1 | 942436 | 942436
100 Amps( set of 2 for 10% booster)
2 | 11 kV G.O switch vertical type 200 Amps (4826/77) | No. | 1 | 4430 | 4430
3 | 11 kV D.O. fuse unit (5792/70) | No. | 1 | 1601 | 1601
4 | 11 kV substation type LA's ( 0/70) | No. | 3 | 345 | 1035
|  | Sub-Total |  |  | 949502
B) | 11 kV four pole structure as per detail P-56 |  |  |  | 77400
|  | Sub-Total |  |  | 1026902
| Storage Charges @ 3.0 % |  |  |  | 30807.06
| Contingencies Charges @ 3.0 % |  |  |  | 30807.06
| Erection charges as per detail P-77 |  |  |  | 71450
| Transportation charges as per statement P-61 |  |  |  | 11330
|  | Total |  |  | 1171296.12
| Departmental Charges @ 11.0 % |  |  |  | 128842.5732
|  | Total |  |  | 1300138.6932
| Less cost of dismantled material as per detail P-59 |  |  |  | -1830
|  | Grand Total |  |  | 1298308.6932
|  | Say Rs in lacs |  |  | 12.9831
PAGE-56
Material cost of 4 Pole Structure on 11 kV line for installation of Auto Voltage Booster
S.No. | Description of item | Iss.No. | Unit | Qty | Rate | Amount
|  | REC STD No. |  |  | Rs. | Rs.
1 | Steel tubular pole 9 mtr long | 2713/80 | No | 4 | 8174 | 32696
2 | Channel iron 2400x100x50x6 mm
I | For line & four pole structure =6 nos.
II | For G.O. switch & G.O. fuse unit =4 nos.
III | For foundation of Auto voltage booster =6 nos.
| total = 16 nos. |  | No | 16 | 1251 | 20016
3 | Half clamps with nuts & bolts |  | No | 14 | 127 | 1778
4 | Full --do-- |  | No | 8 | 202 | 1616
5 | 11 kV strain insulator complete with fittings | 3./71 | No | 6 | 1039 | 6234
6 | 11 kV pin insulators with side tie. Alongwith | G-2/1975 | No | 6 | 93 | 558
helically formed fittings.
7 | Stay set complete with guy grip | G-2/1973 | Set | 5 | 1919 | 9595
8 | Earthing set complete | I-1/1972 | Set | 3 | 1153 | 3459
9 | Danger plate |  | No | 2 | 101 | 202
10 | Barbed wire |  | Kg | 10 | 58 | 580
11 | Set of jumpers with PG clamps (each of 3 nos.) |  | Set | 2 | 333 | 666
| Total |  |  |  |  | 77400
| Say Rs. |  |  |  |  | 77400
PAGE-57
Cost of installation of 1 no. 11 kV 3 ph, Auto Reclosure / 11kV Sectionalizer
S.No. | Description of item | Unit | Qty | Rate | Amount(Rs.)
|  |  |  | Rs. | 11 kV Auto- | 11 kV 3-ph line
[5 empty] | reclosure | Sectionalizer
1 | 11 kV 3-ph auto reclosure | No. | 1 | 463943 | 463943
2 | 11 kV , 3-ph sectionalizer | No. | 1 | 289895 |  | 289895
3 | 11 kV S/Stn type LA's | No. | 3 | 345 | 1035 | 1035
4 | Material cost for double poles structure bed as per detail P-58 | No. | 1 | 43180 | 43180 | 43180
|  | Sub-Total |  |  | 508158 | 334110
| Storage Charges @ 3.0 % |  |  |  | 15244.74 | 10023.3
| Contingencies Charges @ 3.0 % |  |  |  | 15244.74 | 10023.3
| Erection Charges as per detail P-77 |  |  |  | 54380 | 54380
| Transportation Charges as per statement P-61 |  |  |  | 11330 | 11330
|  | Total |  |  | 604357.48 | 419866.6
| Departmental Charges @ 11.0 % |  |  |  | 66479.3228 | 46185.326
|  | Total |  |  | 670836.8028 | 466051.926
| Less cost of dismantled material as per detail P-59 |  |  |  | -1830 | -1830
|  | Grand Total |  |  | 669006.8028 | 464221.926
|  | Say Rs in lacs |  |  | 6.6901 | 4.6422
PAGE-58
Material cost of Double Pole Structure on 11 kV line for installation of Voltage Booster/ Auto line sectionalizer
S.No. | Description of item | Iss.No. | Unit | Qty | Rate | Amount
|  | REC STD No. |  |  | Rs. | Rs.
1 | Steel tubular poles 9 mtr long | 2713/80 | No. | 2 | 8174 | 16348
2 | Channel iron cross arm (2400x100x50mmx6mm) |  | No. | 4 | 1153 | 4612
3 | Angle iron bracing set (750x50x50x6mm) |  | No. | 2 | 170 | 340
4 | Channel iron cross arm (980x100x50x6mm) |  | No. | 2 | 471 | 942
5 | 11 kV strain insulators complete with fittings | 3./71 | No. | 6 | 1039 | 6234
6 | Stay set complete with guy trip | G-2/1976 | Set | 5 | 1919 | 9595
7 | Earthing set complete | T-1/1972 | Set | 2 | 1153 | 2306
8 | Danger plate |  | No. | 2 | 101 | 202
9 | Barbed wire |  | Kg | 8 | 58 | 464
10 | M.S. half clamps with nuts & bolts |  | No. | 2 | 127 | 254
11 | M.S. Full clamps with nuts & bolts |  | No. | 6 | 202 | 1212
12 | Set of jumpers with PG clamps( each set of 3 no.) |  | Set | 2 | 333 | 666
| Total :- |  |  |  |  | 43175
| Say Rs. |  |  |  |  | 43180
PAGE-59
Credit for Material to be Dismantled
S.No. | Description | Unit | Qty | Rate |  | Amount
|  |  |  | Rs. |  | Rs.
1 | 9 mtr long PCC poles | No. | 1 | 2096(1-0.3x15)= | 1153 | 1153
2 | Angle Iron bracing set (750x50x6mm) | No. | 1 | 339(1-0.3x15)= | 186 | 186
3 | Channel Iron cross arm(1500x100x50mm) | No. | 1 | 722(1-0.3x15)= | 397 | 397
4 | 11 kV pin insulator &side tie with pin A/w helically formed | No. | 3 | 93(1-0.3x15)= | 51 | 153
fitting
5 | Top Clamp | No. | 1 | 63(1-0.3x15)= | 35 | 35
| Total:- |  |  |  |  | 1924
| Less 5% dismantling charges |  |  |  |  | -96.2
| Total:- |  |  |  |  | 1827.8
| Say Rs. |  |  |  |  | 1830
Page- 60
Cost of installation of 11 kV Shunt Capacitor Bank
S.No. | Description | Unit | Qty | Rate | Amount(Rs.)
|  |  |  | Rs. | 1.2 MVAR | 1.8 MVAR
1 | 11 kV shunt Capacitor Bank along with series reactor
a | 1.2 MVAR | No. | 1 | 586236 | 586236 | -----
b | 1.8 MVAR | No. | 1 | 807065 | ---- | 807065
|  | Sub-Total |  |  | 586236 | 807065
| Storage Charges @ 3.0 % |  |  |  | 17587.08 | 24211.95
| Contingencies Charges @ 3.0 % |  |  |  | 17587.08 | 24211.95
| Erection charges as per detail P-71 |  |  |  | 33850 | 33850
| Transportation charges 42.18x2(76+33) |  |  |  | 9195.24 | 9195.24
|  | Total |  |  | 664455.4 | 898534.14
| Departmental Charges @ 11.0 % |  |  |  | 73090.094 | 98838.7554
|  | Grand Total |  |  | 737545.494 | 997372.8954
|  | Say Rs in lacs |  |  | 7.3755 | 9.9737

## page 61-64
PAGE-61
Abstract of Transportation Charges
S.No. | Description | Unit | Road | Manual | Unloading & |  | Total
|  |  | Transportation | Transportation | Stacking of material
1 | 33 kV line material
a | Conductor size ACSR 6/1/4.72mm
I | On PCC poles | Km | 15840 | 32640 |  | -- | 48480
II | On steel tubular poles | Km | 15840 | 19010 |  | -- | 34850
III | On 60% PCC & 40% S/T poles | Km | 15840 | 27190 |  | -- | 43030
b | Conductor size AAAC 7/ 4.26mm
I | On PCC poles | Km | 15840 | 32330 |  | -- | 48170
II | On steel tubular poles | Km | 15840 | 18690 |  | -- | 34530
III | On 60% PCC & 40% S/T poles | Km | 15840 | 26870 |  | -- | 42710
2. I | Material for 33/11 kV Sub-Station (Manned) | No. | 297000 | -- | 530x30= | 15900 | 312900
II | Material for 33/11 kV Sub-Station (Un-Manned) | No. | 297000 | -- | 530x30= | 15900 | 312900
III | Material for 33/11 kV Terminal Equipment | No. | 28080 | -- | 530x3= | 4740 | 32820
IV | Material for 11 kV auto Voltage Booster/ | No. | 10800 | -- | 530x1= | 530 | 11330
Sectionalizer/ Autoreclosure
PAGE-62
Transportation Charges for 33 kV line and 33/11 kV Sub-Station
| Average distance of divisional store to central stores (Km) = |  |  | 77
| Average out turn of departmental truck in Rs. Per Km = |  |  | 45
Transportation charges for 1 km of 33 kV line material
| Average distance of divisional store to central stores (Km) = |  |  | 77
| Average lead distance from Divisional store to site of work (Km) = |  |  | 11
Line material of 1 km of 33 kV line length requires
| 2 trip of truck, so total journey of truck = (77+11)x2x2 = |  |  | 352
| Average out turn of Departmental truck in Rs. Per Km = |  |  | 45
| Transportation charges for item of line material (352x45.00) = |  |  | 15840
|  | Say Rs. = |  | 15840
Transportation charges for 33/11 kV Sub-Station (Manned)
| Average distance of central store to Divisional store (Km) = |  |  | 77
| Average lead distance from Divisional store to site of work in Kms = |  |  | 33
Carriage of material for 1 no. 33/11 kV Sub-Station requires
| 30 trips of truck, therefore total journey of truck (30x2(77+33)) = |  |  | 6600
| Transportation Charges for 1no. 33/11kV Sub-Station material (6600x45.00) = |  |  | 297000
|  | Say Rs. = |  | 297000
Transportation charges for 33/11 kV Sub-Station (Un-Manned)
| Average distance of central store to Divisional store (Km) = |  |  | 77
| Average lead distance from Divisional store to site of work in Kms = |  |  | 33
Carriage of material for 1 no. 33/11 kV Sub-Station requires
| 30 trips of truck, therefore total journey of truck (30x2(77+33)) = |  |  | 6600
| Transportation Charges for 1no. 33/11kV Sub-Station material (6600x45.00) = |  |  | 297000
|  | Say Rs.= |  | 297000
PAGE-63
Transportation Charges for Terminal Equipment and 11 kV auto voltage booster/ line sectionalizer/ auto reclosure
Transportation charges for Terminal Equipment
1 | Average distance from central store to Divisional store = |  | 77 kms
2 | Average lead distance from Divisional store to site of work = |  | 27 kms
3 | Carriage of material for 1 no. Terminal Equipment (3 trips); Total = |  | 3x2 ( 77+27) =624
4 | Average out turn of truck = |  | Rs. 45.00 per Km
5 | Transportation charges for 1 set Terminal Equipment = |  | Rs. 624x45.00
|  | Say Rs.= | 28080
Transportation charges for 11 kV auto voltage booster/11 kV line sectionalizer/ 11kV auto reclosure
1 | Average distance from Central store to Divisional store = |  | 77 Kms
2 | Average lead distance from Divisional store to 33/11 kV Sub-Station site = |  | 33 Kms
3 | Average lead distance from 33/11 kV, Sub-Station site to site of installation of 11 kV
| auto voltage booster/ 11 kV line sectionalizer/11kV auto reclosure= |  | 10 Kms
4 | Total journey of truck (1 trip) = |  | 1x2 (77+33+10) =240
5 | Average out turn of truck = |  | Rs. 45.00 per Km
6 | Transportation charges for 1 no. 11kV auto voltage booster
| / 11 kV sectionalizer/11kV auto reclosure = |  | Rs. 240x45.00
| Say Rs.= | 10800
PAGE-64
Average Distance from Divisional Store to Site of Work
Sr. | Name of Sub-Station | Operating Divn. | 33 kV Tapping | Distance from divisional store to |  |  | Remarks
No. |  | to Divn. Store | Point at | Sub-Station (Km) | 33 kV Tapping Point (km)
1 | Chauntra | Joginder Nagar | Bassi | 15 | 5+20 (line length)
2 | Chowari | Dalhousie | Lahru | 45 | 40+5 (line length)
3 | Sandole | Sarkaghat | Jaisinghpur | 40 | 35+7 (line length)
|  | Total :- |  | 100 | 80+32 (line length)
| Average distance of Sub-Station From Divisional store = |  | 100/3=33.33 Say 33 Kms
| Average distance for carriage of 1 km of 33 kV line material = |  | 32/3 = 10.66 Say 11 Kms
| Average distance for carriage of Terminal Equipments = |  | 80/3= 26.66 Say 27 Kms

## page 65
PAGE-65
ANALYSIS OF WORKING DAYS IN THE YEAR
No. of Days
S.NO. | DESCRIPTION
1 | TOTAL NO. OF DAYS IN A YEAR |  |  | 365
2 | SUNDAY HOLIDAYS |  |  | 52
3 | EARNED LEAVE |  |  | 30
4 | CASUAL LEAVE |  |  | 12
5 | GAZZETED HOLIDAYS (RELIGIOUS, NATIONAL, LOCAL) |  |  | 24
6 | WORKING DAYS LOST DUE TO UNFORSEEN CIRCUMSTANCES |  |  | 10
I.e. HEAVY RAINS, ROAD BLOCKADE, SNOWFALL AND
NON AVAILABILITY OF MATERIAL ETC.
7 | TOTAL WORKING DAYS IN A YEAR = 365-(52+30+12+24+10) = |  |  | 237
8 | TOTAL WORKING DAYS IN A MONTH = 237/12= |  |  | 20
A | Details of labour cost per day
S.No | Description | Pay per day | Pay per day | Pay per day | Pay per day
|  | Foreman | Line man | AL/man | T/mate
1 | Pay Band | PB-3 | PB-2 | PB-1 | PB-1
2 | Scale of Pay | 10900-34800 | 6400-20200 | 5100-10680 | 5100-10680
3 | Average Basic pay | 22850 | 13300 | 7890 | 7890
4 | Grade Pay | 4550 | 3050 | 1700 | 1550
5 | DA @ 58% (On Basic+Grade Pay) | 15892 | 9483 | 5562.2 | 5475.2
6 | Compensatory All. | 250 | 250 | 250 | 250
7 | Electricity All. | 88 | 70 | 70 | 70
8 | Medical Allowance | 40 | 40 | 40 | 40
9 | Conveyance All. | 300 | 300 | 150 | 150
10 | Washing All. | 30 | 30 | 30 | 30
11 | House Rent | 250 | 175 | 125 | 125
12 | Risk Allowance | 50 | 50 | 50 | 50
13 | Danger Allowance | 100 | 100 | 50 | 50
14 | TA for 7 day a month
| Foreman @ Rs 84/- per day | 588 | -- | -- | --
| L/Man @ Rs 72/- per day | -- | 504 | -- | --
| ALM @ Rs 60 per day | -- | -- | 420 | --
| T/mate @ Rs 48 per day | -- | -- | -- | 336
| Total :- | 44988 | 27352 | 16337.2 | 16016.2
| Total working days in a month | 20 | 20 | 20 | 20
| Pay per day Rs. | 2249.4 | 1367.6 | 816.86 | 800.81
Say for 2012-13 Rs. |  | 2249 | 1368 | 817 | 801
B | Per day working wages for Beldar
1 | Daily wages (Rs.) |  | = | 130
2 | No. of Sundays in a year |  | = | 52 days
3 | No. of festival Holidays |  | = | 11days
4 | No. of paid holidays in a year I.e. 15th Aug, |  | = | 3 days
2nd Oct & 26th Jan
5 | No. of Casual Leave in a Year |  | = | 12 days
6 | No. of Earned Leave in a Year |  | = | 20 days
7 | Deduction of working hours lost due to unforeseen |  | = | 10 days
circumstances I.e. heavy rains, snow falls,
road blockages & non availability of material.
| Total working day in a year |  | = | 365-(52+11+3+12+20+10) = 257 days
| Actual charges of Beldar per day |  | = | 130x365/257 = | 184.6304
| Say with escalation of 10%for 2012-13 (Rs.) |  | = | 203

## page 67-72
PAGE-67
Abstract for Manual Carriage
Sr. | Description | Foreman @ Rs. |  | 2249 | L/Man @ Rs. |  | 1368 | ALM @ Rs. |  | 817 | T/mate @ Rs. |  | 801 | Beldar @ Rs. |  | 203 | Total
No. |  | No | day | wages | No | day | wages | No | day | wages | No | day | wages | No | day | wages
Manual carriage of material for 1 km of 33 kV line
Assuming avrg lead distance of 1 km from road head
1 | Steel poles 10 M long | -- | -- | -- | -- | -- | -- | -- | -- | -- | 1 | 6 | 4806 | 9 | 6 | 8424 | 13230
2 | PCC poles | -- | -- | -- | -- | -- | -- | -- | -- | -- | 1 | 9 | 7209 | 14 | 9 | 19656 | 26865
3 | M.S. cross arms, bracing sets insulators nuts & bolts Etc. | -- | -- | -- | -- | -- | -- | -- | -- | -- | 1 | 1 | 801 | 11 | 1 | 1716 | 2517
4 | Stay set complete with stay wire | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0 | 5 | 0.75 | 585 | 585
a | ACSR 6/1/ 4.72 cond. | -- | -- | -- | -- | -- | -- | -- | -- | -- | 1 | 1 | 801 | 9 | 1 | 1404 | 2205
b | AAAC 7/4.26 mm | -- | -- | -- | -- | -- | -- | -- | -- | -- | 1 | 1 | 801 | 7 | 1 | 1092 | 1893
c | GI wire 6 SWG | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 0 | 2 | 1.5 | 468 | 468
| Total for S/P (ACSR 6/1/4.72) | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 6408 | -- | -- | 12597 | 19005
| (AAAC 7/4.26) | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 6408 | -- | -- | 12285 | 18693
| or PCC poles (ACSR 6/1/4.72) | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 8811 | -- | -- | 23829 | 32640
| (AAAC 7/4.26) | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 8811 | -- | -- | 23517 | 32328
| Manual carriage for 1 km line with PCC |  | = | ACSR 6/ 1/4.09= |  |  | = | AAAC 7/4.26 mm =
| poles |  | Rs | 32640 |  |  |  |  | 32328
| Say Rs |  |  | 32640 |  |  |  |  | 32330
| Manual carriage for 1 km line with S/T |  | = | 19005 |  |  |  |  | 18693
| poles | Say Rs. |  | 19010 |  |  |  |  | 18690
PAGE-68
Detailed analysis of Labour Rates for 33 kV line with 6/1/4.72 mm ACSR/ AAAC 7/4.26
|  | Foreman @ of Rs. |  | 2249 | L/Man @ of Rs. |  | 1368 | ALM @ of Rs. |  | 817 | T/mate @ of Rs. |  | 801 | Beldar @ of Rs. |  | 203 | Total
SR. | Description | No | No. of days | wages | No | No. of days | wages | No | No. of days | wages | No | No. of days | wages | No | No. of days | wages | S/C | D/C
No.
A) | Surveying & Stacking(33 kV line)
a | Preliminary, actual surveying profiling | 1 | 6 | 13494 | 2 | 6 | 16416 | -- | -- | 0 | -- | -- | 0 | 6 | 6 | 7308 | 37218 | 37218
& final survey of 1 km of line
b | Stacking of 1 km of line work | -- | -- | 0 | 2 | 2 | 5472 | -- | -- | 0 | -- | -- | 0 | 6 | 2 | 2436 | 7908 | 7908
c | Camp shifting | 1 | 0.5 | 1124.5 | 2 | 0.5 | 1368 | -- | -- | 0 | -- | -- | 0 | 6 | 0.5 | 609 | 3101.5 | 3101.5
| Total :- | -- | -- | 14618.5 | -- | -- | 23256 | -- | -- | 0 | -- | -- | 0 | -- | -- | 10353 | 48227.5 | 48227.5
[15 empty] | Say Rs. |  | 48230 | 48230
B) | Erection of double PCC pole structure
a | Digging of pits | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 1 | 1 | 801 | 6 | 0.66667 | 812 | 1613 | 1613
b | Erection of two pole structure | 1 | 0.25 | 562.25 | -- | -- | 0 | 1 | 0.25 | 204.25 | 2 | 0.25 | 400.5 | 12 | 0.25 | 609 | 1776 | 1776
c | Drilling of poles in X-arms cross bracing | -- | -- | 0 | -- | -- | 0 | 1 | 0.125 | 102.125 | 2 | 0.125 | 200.25 | -- | -- | 0 | 302.375 | 604.75
d | Fixing of X-arm string insul. Cross bracing | 1 | 0.5 | 1124.5 | 1 | 0.5 | 684 | 1 | 0.5 | 408.5 | 1 | 0.5 | 400.5 | -- | -- | 0 | 2617.5 | 4110.5
e | Fixing of barbed wire danger plate etc. | -- | -- | 0 | -- | -- | 0 | 1 | 0.25 | 204.25 | 1 | 0.25 | 200.25 | 1 | 0.25 | 50.75 | 455.25 | 455.25
f | Filling of pits & ramming | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 1 | 0.5 | 400.5 | 4 | 0.5 | 406 | 806.5 | 806.5
g | Painting of steel cross arms etc. | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 2 | 0.5 | 203 | 203 | 406
| Total :- |  |  | 1686.75 |  |  | 684 |  |  | 919.125 |  |  | 2403 |  |  | 2080.75 | 7773.625 | 9772
[15 empty] | Say Rs. |  | 7770 | 9770
C) | Erection of double S/T pole structure | -- | 0.75 | 1686.75 | -- | 0.5 | 684 | -- | -- | 919.125 | -- | -- | 2403 | -- | -- | 2080.75 | 7773.625
(As per head "B" for PCC (9.75 M)
a | Placing of templates & filling of concrete | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 1 | 0.5 | 400.5 | 2 | 0.5 | 203 | 603.5 | 603.5
b | painting of poles | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 2 | 0.5 | 203 | 203 | 203
| Total :- |  |  | 1686.75 |  |  | 684 |  |  | 919.125 |  |  | 2803.5 |  |  | 2486.75 | 8580.125 | 8580.125
[15 empty] | Say Rs. |  | 8580 | 8580
D) | Erection of double PCC pole structure (Dead End)
a | (9.75 M , dead end) as per S/head B | -- | 0.75 | 1686.75 | -- | 0.5 | 684 | -- | -- | 919.125 | -- | -- | 2403 | -- | -- | 2080.75 | 7773.625 | 7773.625
b | Fixing of additional cross-arms for dead | 1 | 0.25 | 562.25 | 1 | 0.25 | 342 | 1 | 0.25 | 204.25 | 1 | 0.25 | 200.25 | -- | -- | 0 | 1308.75 | 1308.75
end, 3 no. addl. String insulator
dead end clamp only
c | Painting of cross arm | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 1 | 0.125 | 25.375 | 25.375 | 25.375
| Total :- |  |  | 2249 |  |  | 1026 |  |  | 1123.375 |  |  | 2603.25 |  |  | 2106.125 | 9107.75 | 9107.75
[15 empty] | Say Rs. |  | 9110 | 9110
E) | Erection of double pole S/T poles (Dead End)
structure (dead end 9.75 M long)
a | As per sub head (C) | -- | -- | 1686.75 | -- | -- | 684 | -- | -- | 919.125 | -- | -- | 2803.5 | -- | -- | 2486.75 | 8580.125 | 8580.125
b | As per item b+c of S/head (D) | -- | -- | 562.25 | -- | -- | 342 | -- | -- | 204.25 | -- | -- | 200.25 | -- | -- | 25.375 | 1334.125 | 1334.125
| Total :- |  |  | 2249 |  |  | 1026 |  |  | 1123.375 |  |  | 3003.75 |  |  | 2512.125 | 9914.25 | 9914.25
[15 empty] | Say Rs. |  | 9910 | 9910
F | Earthing of 33 kV line
a | Digging of pit | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 6 | 1 | 1218 | 7314.875 | 7314.875
b | Fixing of earth red, clamp earth wire and | -- | -- | 0 | 1 | 0.5 | 684 | 1 | 0.5 | 408.5 | -- | -- | 0 | 2 | 0.5 | 203 | 1295.5 | 1295.5
connecting to the structure
c | Filling of the pit with material & earth | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 1 | 0.25 | 200.25 | 6 | 0.25 | 304.5 | 504.75 | 504.75
| Total :- |  |  | 0 |  |  | 684 |  |  | 408.5 |  |  | 200.25 |  |  | 1725.5 | 3018.25 | 3018.25
[15 empty] | Say Rs. |  | 3020 | 3020
PAGE-69
G | Erection of stay set of 33 kV lines
a | Digging of pit | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 1 | 0.25 | 200.25 | 4 | 0.25 | 203 | 403.25 | 403.25
b | Filling of stay rod, its template etc. | 1 | 0.125 | 281.125 | 1 | 0.125 | 171 | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 452.125 | 452.125
c | Filling of the pit | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 1 | 0.25 | 200.25 | 4 | 0.25 | 203 | 403.25 | 403.25
d | Nuzzling of stay rod, and its lighting | 1 | 0.125 | 171 | 1 | 0.125 | 171 | -- | -- | 0 | 1 | 0.125 | 100.125 | -- | -- | 0 | 442.125 | 442.125
| Total :- |  |  | 452.125 |  |  | 342 |  |  | 0 |  |  | 500.625 |  |  | 406 | 1700.75 | 1700.75
[15 empty] | Say Rs. |  | 1700 | 1700
H | Fixing of jumpers (1 set) for 33 kV line | 1 | 0.25 | 341.5 | 1 | 0.25 | 220.75 | 1 | 0.25 | 162 | -- | -- | 0 | 1 | 0.25 | 39 | 763.25 | 1526.5
I | Stringing of 1 km of line (33 kV) | [13 empty] | Say Rs. |  | 760 | 1520
1 | GI wire
a | Laying of GI wire | 1 | 0.125 | 281.125 | 1 | 0.125 | 171 | 2 | 0.125 | 204.25 | 2 | 0.125 | 200.25 | 5 | 0.125 | 126.875 | 983.5 | 983.5
b | Straining and sagging | 1 | 0.375 | 843.375 | 1 | 0.375 | 513 | 2 | 0.375 | 612.75 | 2 | 0.375 | 600.75 | 5 | 0.375 | 380.625 | 2950.5 | 2950.5
c | Binding with insulator | 0 | 0 | 0 | 1 | 1.25 | 1710 | 2 | 1.25 | 2042.5 | 0 | 0 | 0 | 0 | 0 | 0 | 3752.5 | 3752.5
| Total :- | 2 | 0.5 | 1124.5 | 3 | 1.75 | 2394 | 6 | 1.75 | 2859.5 | 4 | 0.5 | 801 | 10 | 0.5 | 507.5 | 7686.5 | 7686.5
[15 empty] | Say Rs. |  | 7690 | 7690
2 | 100 mm2 33 kV (SC) line
a | Laying of conductor ACSR | 1 | 0.625 | 1405.625 | 2 | 0.625 | 1710 | 2 | 0.625 | 1021.25 | 2 | 0.625 | 1001.25 | 12 | 0.625 | 1522.5 | 6660.625 | 6660.625
| (AAAC) | 1 | 0.625 | 1405.625 | 2 | 0.625 | 1710 | 2 | 0.625 | 1021.25 | 2 | 0.625 | 1001.25 | 10 | 0.625 | 1268.75 | 6406.875 | 6406.875
b | Straining and sagging ACSR | 1 | 0.625 | 1405.625 | 2 | 0.625 | 1710 | 2 | 0.625 | 1021.25 | 2 | 0.875 | 1401.75 | 12 | 0.875 | 2131.5 | 7670.125 | 7670.125
| (AAAC) | 1 | 0.625 | 1405.625 | 2 | 0.625 | 1710 | 2 | 0.625 | 1021.25 | 2 | 0.875 | 1401.75 | 10 | 0.875 | 1776.25 | 7314.875 | 7314.875
c | Winding with insul. fixing of bird guards | -- | -- | 0 | 2 | 0.5 | 1368 | 2 | 0.5 | 817 | -- | -- | 0 | -- | -- | 0 | 2185 | 2185
| Total ACSR 6/1/4.72 mm | -- | -- | 2811.25 | -- | -- | 4788 | -- | -- | 2859.5 | -- | -- | 2403 | -- | -- | 3654 | 16515.75 | 16515.75
[15 empty] | Say Rs. |  | 16520 | 16520
| Total AAAC7/4.26 mm | -- | -- | 2811.25 | -- | -- | 4788 | -- | -- | 2859.5 | -- | -- | 2403 | -- | -- | 1370.25 | 15906.75 | 15906.75
[15 empty] | Say Rs. |  | 15910 | 15910
J) | Road path stream etc.
1 | Erection of 2 no. PCC poles 8 M long
a | Digging of pits | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 6 | 0.33333 | 406 | 406 | 406
b | Erection of poles | -- | -- | 0 | 1 | 0.4 | 547.2 | 1 | 0.4 | 326.8 | 2 | 0.4 | 640.8 | 4 | 0.66667 | 541.3333 | 2056.1333 | 2056.1333
c | Filling of pits & ramming | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 1 | 1 | 203 | 203 | 203
2 | Erection of 2 no. stay sets (LT)
a | Digging of pits | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 1 | 0.33333 | 267 | 6 | 0.33333 | 406 | 673 | 673
b | Fixing of stay rod, nuzzling & tightening | -- | -- | 0 | 1 | 0.25 | 342 | 1 | 0.25 | 204.25 | -- | -- | 0 | -- | -- | 0 | 546.25 | 546.25
c | Filling of pits | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 1 | 0.33333 | 267 | 2 | 0.5 | 203 | 470 | 470
3 | Earthing (s) 2 no.
a | Digging of pits | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 1 | 0.33333 | 267 | 6 | 0.25 | 304.5 | 571.5 | 571.5
b | Fixing of earth rod, earth wire& conn. | -- | -- | 0 | 1 | 0.25 | 342 | 1 | 0.25 | 204.25 | -- | -- | 0 | -- | -- | 0 | 546.25 | 546.25
c | Filling of pits | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 1 | 0.33333 | 267 | 1 | 1 | 203 | 470 | 470
d | Stringing of catenary wire & filling with | -- | -- | 0 | 1 | 0.125 | 171 | 1 | 0.125 | 102.125 | -- | -- | 0 | 4 | 0.125 | 101.5 | 374.625 | 374.625
poles & earth connections
| Total :- |  |  | 0 |  |  | 1402.2 |  |  | 837.425 |  |  | 1708.8 |  |  | 2368.3333 | 6316.7583 | 6316.7583
[15 empty] | Say Rs. |  | 6320 | 6320
PAGE-70
Detailed analysis of Labour Charges for 33/11 kV Sub-Station
|  | Foreman @ of Rs. |  | 2249 | L/Man @ of Rs. |  | 1368 | ALM @ of Rs. |  | 817 | T/mate @ of Rs. |  | 801 | Beldar @ of Rs. |  | 203
SR. | Description | No | No. of days | wages | No | No. of days | wages | No | No. of days | wages | No | No. of days | wages | No | No. of days | wages | Total
No.
I | Laying of earth material rods & pipe
a | Excavation for laying earth metal | 1 | 0.5 | 1124.5 | 1 | 1 | 1368 | -- | -- | 0 | 1 | 6 | 4806 | 20 | 6 | 24360 | 31658.5
at 0.75M depth (37xM)= 22nos. & (25x1)
b | Laying fault welding Erection earth riser | 1 | 3 | 6747 | 1 | 3 | 4104 | 1 | 3 | 2451 | 1 | 3 | 2403 | 6 | 3 | 3654 | 19359
&painting other treatment after welding.
c | Digging of 3 M deep pits for solid earth | -- | -- |  | -- | -- | 0 | -- | -- | 0 | 1 | 6 | 4806 | 6 | 2 | 2436 | 7242
rods of Mat ( 4 no.)
d | Fixing of solid earth rods with earth mat | -- | -- | 0 | 1 | 1 | 1368 | 1 | 1 | 817 | -- | -- | 0 | 2 | 1 | 406 | 2591
e | Digging of 3.15 M deep earth pit for 11 no. | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 6 | 8 | 9744 | 9744
pipe type electrodes for earthing
f | Fixing of pipe type electrodes with earth | 1 | 1 | 2249 | 1 | 1 | 1368 | 1 | 1 | 817 | -- | -- | 0 | 5 | 1 | 1015 | 5449
mat
g | Filling of earth excavated item a,b & d | -- | -- | 0 | 2 | 3 | 8208 | -- | -- | 0 | 2 | 3 | 4806 | 11 | 3 | 6699 | 19713
filling of item c, e, to be done with charcoal
& salt preparation of demanded pits
for later treatment for pipe
| Total :- | -- | -- | 10120.5 | -- | -- | 16416 | -- | -- | 4085 | -- | -- | 16821 | -- | -- | 48314 | 95756.5
[15 empty] | Say Rs. |  | 95760
II | Erection of R.S. joists
10000x225x150 mm
a | Digging of pit | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 1 | 0.5 | 400.5 | 5 | 0.5 | 507.5 | 908
b | Erection of R.S. 10000x225x150 mm | 1 | 0.5 | 1124.5 | -- | -- | 0 | 1 | 0.5 | 408.5 | 1 | 0.5 | 400.5 | 6 | 0.5 | 609 | 2542.5
with muff complete etc.
c | Filling of pit | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 5 | 0.25 | 253.75 | 253.75
| Total :- |  |  | 1124.5 |  |  | 0 |  |  | 408.5 |  |  | 801 |  |  | 1370.25 | 3704.25
[15 empty] | Say Rs. |  | 3704
III | Erection of each cross | 1 | 0.25 | 562.25 | 1 | 0.25 | 342 | -- | -- | 0 | 1 | 0.25 | 200.25 | 2 | 0.25 | 101.5 | 1206
| arms of various sizes including | [13 empty] | Say Rs. |  | 1210
drilling of pole&fixing clamps etc.
IV | Foundation of VCB
a | Digging of pit | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 1 | 0.25 | 200.25 | 3 | 0.25 | 152.25 | 352.5
b | PCC masonry foundation | 1 | 1 | 2249 | -- | -- | 0 | 1 | 1 | 817 | 1 | 1 | 801 | 6 | 1 | 1218 | 5085
c | Erection of steel structure | 1 | 1 | 2249 | 1 | 1 | 1368 | 1 | 1 | 817 | 1 | 1 | 801 | -- | -- | 0 | 5235
| Total :- |  |  | 4498 |  |  | 1368 |  |  | 1634 |  |  | 1802.25 |  |  | 1370.25 | 10672.5
[15 empty] | Say Rs. |  | 10673
V | Foundation of transformer
a | Digging of pit | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 1 | 1 | 801 | 12 | 1 | 2436 | 3237
b | PRCC masonry foundation including | 1 | 1 | 2249 | 1 | 1 | 1368 | 1 | 1 | 817 | 1 | 1 | 801 | 10 | 1 | 2030 | 7265
filling of pit & laying of rail etc.
| Total :- |  |  | 2249 |  |  | 1368 |  |  | 817 |  |  | 1602 |  |  | 4466 | 10502
[15 empty] | Say Rs. |  | 10500
PAGE-71
VI | Laying of trenches (per Mtrs.)
a | Earth excavation | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 3 | 0.66667 | 406 | 406
b | trench lining etc. | 1 | 0.5 | 1124.5 | 1 | 0.5 | 684 | -- | -- | 0 | 1 | 0.5 | 400.5 | 3 | 0.5 | 304.5 | 2513.5
| Total :- |  |  | 1124.5 |  |  | 684 |  |  | 0 |  |  | 400.5 |  |  | 710.5 | 2919.5
[15 empty] | Say Rs. |  | 2920
VII | Erection of 1 set of Bus bar | 1 | 0.66667 | 1499.3333 | -- | -- | 0 | 1 | 0.66667 | 544.6667 | 2 | 0.66667 | 1068 | -- | -- | 0 | 3112
[15 empty] | Say Rs. |  | 3110
VIII | Installation of isolator | 2 | 0.875 | 3935.75 | 4 | 0.875 | 4788 | 4 | 0.875 | 2859.5 | -- | -- | 0 | 4 | 0.875 | 710.5 | 12293.75
[15 empty] | Say Rs. |  | 12290
IX | Installation of Lightening Arrestors | 1 | 0.375 | 843.375 | 1 | 0.375 | 513 | -- | -- | 0 | 1 | 0.375 | 300.375 | -- | -- | 0 | 1656.75
[15 empty] | Say Rs. |  | 1660
X | Installation of PT's (single phase) | 1 | 0.375 | 843.375 | 2 | 0.375 | 1026 | -- | -- | 0 | 2 | 0.375 | 600.75 | 2 | 0.375 | 152.25 | 2622.375
[15 empty] | Say Rs. |  | 2620
XI | Installation of D.O. fuse unit | 1 | 0.75 | 1686.75 | 1 | 0.75 | 1026 | 2 | 0.75 | 1225.5 | 2 | 0.75 | 1201.5 | -- | -- | 0 | 5139.75
[15 empty] | Say Rs. |  | 5140
XII | Installation & commissioning of power | 3 | 5 | 33735 | 3 | 5 | 20520 | 3 | 5 | 12255 | 3 | 5 | 12015 | 18 | 1 | 3654 | 82179
| transformer (1 no. including dehydration) | [13 empty] | Say Rs. |  | 82180
XIII | Installation of S/Stn transformer | 3 | 4 | 26988 | 3 | 4 | 16416 | 3 | 4 | 9804 | 3 | 4 | 9612 | 12 | 0.5 | 1218 | 64038
[15 empty] | Say Rs. |  | 64040
XIV | Installation of VCB with CT 11 kV voltage | 3 | 2 | 13494 | 3 | 2 | 8208 | 3 | 2 | 4902 | 3 | 2 | 4806 | 6 | 2 | 2436 | 33846
| booster 11 kV line sectionalizer | [13 empty] | Say Rs. |  | 33850
XV | Erection of 1 set of jumper inclu. PG clamps | 1 | 0.25 | 562.25 | 1 | 0.25 | 342 | 1 | 0.25 | 204.25 | 1 | 0.25 | 200.25 | -- | -- | 0 | 1308.75
[15 empty] | Say Rs. |  | 1310
XVI | Connection set | 1 | 0.25 | 562.25 | 1 | 0.25 | 342 | 1 | 0.25 | 204.25 | 1 | 0.25 | 200.25 | -- | -- | 0 | 1308.75
[15 empty] | Say Rs. |  | 1310
XVII | Installation of 11 kV incoming panel | 3 | 5 | 33735 | 3 | 5 | 20520 | 3 | 6 | 14706 | -- | -- | 0 | 6 | 1 | 1218 | 70179
[15 empty] | Say Rs. |  | 70180
XVIII | Laying of control cable | 2 | 3 | 13494 | 2 | 3 | 8208 | 2 | 3 | 4902 | 2 | 3 | 4806 | -- | -- | 0 | 31410
[15 empty] | Say Rs. |  | 31410
XIX | Installation of 11 kV out going feeder | 3 | 5 | 33735 | 3 | 5 | 20520 | 3 | 6 | 14706 | -- | -- | 0 | 6 | 1 | 1218 | 70179
| panel or bus coupler | [13 empty] | Say Rs. |  | 70180
XX | Laying of power cable (per no. of 50M)
a | Digging of earth | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 8 | 0.5 | 812 | 812
b | Laying of cable in bricks & sand | 1 | 0.75 | 1686.75 | 1 | 0.75 | 1026 | -- | -- | 0 | -- | -- | 0 | 8 | 0.75 | 1218 | 3930.75
c | Filling of earth | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 4 | 0.5 | 406 | 406
| Total :- |  |  | 1686.75 |  |  | 1026 |  |  | 0 |  |  | 0 |  |  | 2436 | 5148.75
[15 empty] | Say Rs. |  | 5150
XXI | Connecting the cable ends to cable | 2 | 0.75 | 3373.5 | 2 | 0.75 | 2052 | -- | -- | 0 | 2 | 0.75 | 1201.5 | -- | -- | 0 | 6627
| box or epoxy kit | [13 empty] | Say Rs. |  | 6630
PAGE-72
XXII | Installation of Stn.
a | Battery set with trickle charger & rectifier. | 4 | 5 | 44980 | 4 | 5 | 27360 | 4 | 5 | 16340 | -- | -- | 0 | 6 | 2 | 2436 | 91116
b | A.C. control board | 2 | 2 | 8996 | 2 | 2 | 5472 | 2 | 2 | 3268 | -- | -- | 0 | 6 | 1 | 1218 | 18954
c | Fire fighting equipment | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 1 | 0.5 | 400.5 | 3 | 0.5 | 304.5 | 705
| Total :- |  |  | 53976 |  |  | 32832 |  |  | 19608 |  |  | 400.5 |  |  | 3958.5 | 110775
[15 empty] | Say Rs. |  | 110780
XXIII | Yard lighting | 3 | 0.875 | 5903.625 | 3 | 0.875 | 3591 | 3 | 0.875 | 2144.625 | 3 | 0.875 | 2102.625 | 18 | 0.25 | 913.5 | 14655.375
[15 empty] | Say Rs. |  | 14660
XXIV | Erection of yard fencing ( 1 Mtr)
a | Digging of pit | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | -- | -- | 0 | 2 | 0.5 | 203 | 203
b | Erection of angle iron supports | -- | -- | 0 | 1 | 0.75 | 1026 | 1 | 0.75 | 612.75 | -- | -- | 0 | 2 | 0.75 | 304.5 | 1943.25
c | Filling the pit & muffing of angle iron | -- | -- | 0 | 1 | 0.5 | 684 | 1 | 0.5 | 408.5 | -- | -- | 0 | 2 | 0.5 | 203 | 1295.5
support
d | Fixing of barbed wire | -- | -- | 0 | -- | -- | 0 | 1 | 0.5 | 408.5 | -- | -- | 0 | 1 | 0.5 | 101.5 | 510
| Total :- |  |  | 0 |  |  | 1710 |  |  | 1429.75 |  |  | 0 |  |  | 812 | 3951.75

## page 73-78
PAGE-73
Erection/ Labour charges for construction of 1 km of 33 kV line on 9.75/10 M long Double Pole Structure
with ACSR 6/1/4.72 mm Conductor with single continuous earth wire .
S.No. | Description | Refer S/head | Qty. | Unit | Rate (Rs.) |  | Amount (in Rs.)
[5 empty] | S/C | D/C | PCC Poles | S/T Poles | 40% S/T+ 60 % PCC Poles | S/T Poles (D/C)
1 | Surveying & stacking of line | A | 1 | Km | 48230 | 48230 | 48230 | 48230 | 48230 | 48230
2 | Erection of PCC Pole structure( susp) | B | 4 | No. | 7770 | 9770 | 31080 |  |  | 39080
3 | Erection of S/T Pole structure( susp) | C | 4 | No. | 8580 | 8580 |  | 34320 |  | 34320
4 | Erection of 60% PCC & 40% S/T Pole structure( susp) | -- | 4 | No. | 8094 |  |  |  | 32376
5 | Erection of PCC Pole structure( Dead end) | D | 2 | No. | 9110 | 9110 | 18220 |  |  | 18220
6 | Erection of S/T Pole structure( dead end) | E | 2 | No. | 9910 | 9910 |  | 19820 |  | 19820
7 | Erection of 60% PCC & 40% S/T Pole structure(dead end) | -- | 2 | No. | 9430 |  |  |  | 18860
STAY SET COMPLETE
One suspension structure with angle =5 no.
Two dead end with angle =10 no.
| Total =11 no. | G | 15 | No. | 1700 | 1700 | 25500 | 25500 | 25500 | 25500
8 | Earthing of line at every alternate structure | F | 3 | No. | 3020 | 3020 | 9060 | 9060 | 9060 | 9060
9 | Road path stream crossing guarding ( avrg 2 no./km) | J | 2 | No. | 6320 | 6320 | 12640 | 12640 | 12640 | 12640
10 | Stringing of telephone & earth wire (GI No. 6 SWG) | I)1 | 3 | No. | 7690 | 7690 | 23070 | 23070 | 23070 | 23070
11)I | Stringing of 100 mm2 6/1/4.72 mm or 6/1/4.09 ACSR cond. | I)2 | 3 | No. | 16520 | 16520 | 49560 | 49560 | 49560 | 49560
II | Stringing of 100 mm2 7/4.26 mm AAAC cond. | I)2 | 3 | No. | 15910 | 15910 | 47730 | 47730 | 47730 | 47730
12 | Making jumpers | H | 2 | Set | 760 | 1520 | 1520 | 1520 | 1520 | 3040
[5 empty] | Total |  | 218880 | 221890 | 218986 | 280710
PAGE-74
Erection charges for 33/11 kV Sub-Station with common/ independent breaker control of Transformer
33/11 kV Sub-Station with
S.No. | Description | S/head | Unit | Rate (Rs.) | Common Breaker control of Transformer |  |  | Independent Breaker control of Transformer
[5 empty] | Qty | Amount (Rs.) |  | Qty | Amount (Rs.)
1 | Laying of earth mat, earthing rod & pipes | I | No. | 95760 | 1 | 95760 |  | 1 | 95760
2 | Erection of super structure & busbar
a | Erection of R.S. joists | II | No. | 3704 | 18 | 66672 |  | 18 | 66672
b | Erection of cross arms | III | No. | 1210 | 29 | 35090 |  | 29 | 35090
c | Erection of T-set | XV | No. | 1310 | 25 | 32750 |  | 27 | 35370
d | Erection of Jumper sets | XVI | No. | 1310 | 12 | 15720 |  | 12 | 15720
e | Erection of one set of bus bar | VII | No. | 3110 | 9 | 27990 |  | 9 | 27990
3 | Erection of foundations
a | Power Transformer | V | No. | 10500 | 2 | 21000 |  | 2 | 21000
b | Circuit breaker (VCB) | IV | No. | 10673 | 1 | 10673 |  | 1 | 10673
c | Laying of trenches | VI | Mtrs. | 2920 | 155.3 | 453476 |  | 155.3 | 453476
4 | Installation of equipment
a | Isolators | VIII | No. | 12290 | 8 | 98320 |  | 9 | 110610
b | Lightening Arresters | IX | No. | 1660 | 9 | 14940 |  | 9 | 14940
c | PT's (1-phase) | X | No. | 2620 | 3 | 7860 |  | 3 | 7860
d | D.O. fuse unit | XI | No. | 5140 | 1 | 5140 |  | 1 | 5140
e | Circuit Breaker ( V/SF6 CB) with CT's | XIV | No. | 33850 | 1 | 33850 |  | 1 | 33850
f | Station Transformer | XIII | No. | 64040 | 1 | 64040 |  | 1 | 64040
g | Power Transformer | XII | No. | 82180 | 2 | 164360 |  | 2 | 164360
h | 11 kV incoming panel with PT's | XVII | No. | 70180 | 2 | 140360 |  | 2 | 140360
I | 11kV bus coupler | XIX | No. | 70180 | 1 | 70180 |  | 1 | 70180
j | 11 kV out going panels | XIX | No. | 70180 | N | 70180N |  | N | 70180N
5 | Laying of control cables set (for 50 M) | XVIII | Set | 31410 | 12 | 376920 |  | 12 | 376920
6 | Laying of power cables set (for 50 M) | XX | Set | 5150 | 2+N | 10300+5150N |  | 2+N | 10300+5150N | 10300
7 | Connecting the power cable to cable for epoxy | XXI | No. | 6630 | 2(2+N) | 26520+13260N |  | 2(2+N) | 26520+13260N | 26520
8 | Installation of Sub-Station auxiliaries | XXII | No. | 110780 | 1 | 110780 |  | 1 | 110780 | 13260
9 | Erection fencing | XXIV | No. | 3951.75 | 378 | 1493761.5 |  | 378 | 1493761.5
10 | Erection of yard lighting | XXIII | No. | 14660 | 1 | 14660 |  | 1 | 14660
| Total |  |  | 88590 | N + | 3391122.5 | 88590 | N + | 3406032.5
PAGE-75
Erection of 11 kV yard for 4 feeder, therefore N no. feeder
S.No. | Description | REF | Unit | Rate(Rs.) | Qty | Amount (Rs.)
a | Erection of structures | II | No. | 3704 | 5 | 18520
b | Erection of cross arms | III | No. | 1210 | 40 | 48400
c | Erection of set of Busbar | VII | No. | 3110 | 1 | 3110
d | Erection of jumpers | XV | No. | 1310 | 24 | 31440
e | Erection of isolators | VIII | No. | 12290 | 8 | 98320
f | Erection of LA's | IX | No. | 1660 | 12 | 19920
|  |  |  | Sub-Total :- |  | 219710
| Erection Charges for Single feeder = Sub-Total / 4 = | 54927.5
| Say Rs. | 54930
| Erection Charges for N feeder = N x Sub-Total /4 = | 54930.00 x N
Erection Charges for 33/11 kV sub-station with common breaker control of Transformer
|  | 4 nos. | 5 nos. | 6 nos. | 7 nos. | 8 nos.
| Total | 3965202.5 | 4108722.5 | 4252242.5 | 4395762.5 | 4539282.5
| Say Rs | 3965200 | 4108700 | 4252200 | 4395800 | 4539300
Erection Charges for 33/11 kV Sub-Station with Independent control of Transformer
|  | 4 nos. | 5 nos. | 6 nos. | 7 nos. | 8 nos.
| Total | 3980112.5 | 4123632.5 | 4267152.5 | 4410672.5 | 4554192.5
| Say Rs | 3980100 | 4123600 | 4267200 | 4410700 | 4554200
PAGE-76
Erection Charges for Terminal Equipment & Allied Material for each of 33 kV out going Feeder
Amount for 33/11 kV S/Stn
S.No. | Description | Refer S/head | Unit | Qty | Rate (Rs.) | PT's already installed | PT's not installed
A | Earthing | I (e+f) | Job | 1 | 15193 | 15193 | 15193
B | Foundation of VCB | IV | Job | 1 | 10673 | 10673 | 10673
C | Laying of trenches O.B. type | VI | M | 9 | 2920 | 26280 | 26280
D | Laying of control cables (set of 50 M) | XVIII | 50 M | 76 | 31410 | 47743.2 | 47743.2
E | Erection of super structures
a | Erection of R.S. joists | II | Job | 2 | 3704 | 7408 | 7408
b | Erection of cross arms | III | Job | 9 | 1210 | 10890 | 10890
c | Erection of Jumper sets | XV | Job | 9 | 1310 | 11790 | 11790
d | Erection of a set of bus bar | VII | Job | 1 | 3110 | 3110 | 3110
Erection of equipment
I | Isolator | VIII | Job | 3 | 12290 | 36870 | 36870
II | LA's | IX | Job | 3 | 1660 | 4980 | 4980
III | PT's | X | Job | 3 | 2620 |  | 7860
IV | Circuit breaker with CT's & CR panels | XIV | Job | 1 | 33850 | 33850 | 33850
[5 empty] | Total | 208787.2 | 216647.2
[5 empty] | Say Rs. | 208790 | 216650
PAGE-77
Erection Charges for 11 kV Auto voltage Booster/Sectionalizer/ Auto reclosure
S. | Description | Refer S/head |  | Unit | Qty | Rate | Amount | Amount
No. |  | RE Cost Data | SI Cost Data |  |  | Rs. | 11 kV auto | 11 kV line
[7 empty] | voltage | sectionalizer
[7 empty] | booster | reclosure
1 | Erection of Double PCC Poles Structures (9 M) | S/head A-3 |  | No. | 1 | 4777 | 4777
2 | Erection of Single Pole (9 M) including fixing of X-arms | S/head A-1 & A-3(b) |  | No. | 1 | 3260.25 | 3260.25 | 3260.25
insulator of cross bracing set etc.
3)a | Preparation of Platform Structure | S/head C 3 |  | No. | 1 | 2436 | 2436 | 2436
3)b | Erection of Platform | S/head C 6 |  | No. | 1 | 2096.5 | 2096.5 | 2096.5
4 | Erection of GO switch |  | VIII | No. | 1 | 12290 | 12290
5 | Erection of LA's |  | IX | No. | 3 | 1660 | 4980 | 4980
6 | Erection of Jumpers (set) |  | XV | No. | 2 | 1310 | 2620 | 2620
7 | Erection of D.O. fuse unit |  | XI | No. | 1 | 5140 | 5140 | 5140
8 | Installation of 11 kV voltage booster/ line sectionalizer/ |  | XIV | No. | 1 | 33850 | 33850 | 33850
11 kV auto reclosure
[6 empty] | Total | 71449.75 | 54382.75
[6 empty] | Say Rs. | 71450 | 54380

## ANYLIS 79-80
PAGE-78
ANALYSIS Page --1
Construction of 1 km of 33 kV line with ACSR (100 mm sqr. Al. equivalent) conductor on 9.75 mtr./10 mtr. long
PCC/Steel Tubular or 60 % PCC & 40 % S/T Pole (Double pole structures) with single continuous earth wire
Sr No. | Description | Unit | Qty | Amount (Rs.)
1 | Angle iron 2240*65*65*6 mm cross arm for earth wires (2.24*6.8*Rs.51) | No. | 1 | 765.6593 |  | 0 |  | 13.92 | 403.68 | 60.552 | 464.232
2 | M.S. cross bracing set (consisting of 1800x65X65x6 mm- 2 Nos | [6 empty] | 13.92 | 403.68 | 60.552 | 464.232
| and 2700x50x50x6 mm-2 Nos. of M.S Angle Irons including clamps and bolts.) | [6 empty] | 17.76 | 515.04 | 77.256 | 592.296
| (1.8*6.8*51*2+2.7*4.5*51*2) | No. | 1 | 2451.9999 |  | 0 |  | 34.8 | 1009.2 | 151.38 | 1160.58
2217.108
3 | M.S. channel iron cross arm consisting of 4000x125x65x6 mm | No. | 1 | 2633.9646 |  | 2633.9646 |  | 2133.74
(4*13.1*51)
ANALYSIS Page --34
A | CROSS ARMS
1 | 3.75 long M.S. channel iron 100X50X6 mm 9.56kg/mtr. Cross arms for S/Stn. | No. | 1 | 1802.054
2 | 3.75 long M.S. angle iron 50X50X6 mm 4.5 kg/mtr. Cross arms for S/Stn. | No. | 1 | 848.2472
B | CLAMPS
3 | M.S. half clamps with nuts & bolts for S/Stn | No | 1 | 127
4 | M.S. full clamps with nuts & bolts for S/Stn | No | 1 | 202
--
PAGE-79
ANALYSIS Page --43
A) | Expended metal fencing around switchyard
1 | M.S. angle iron 65x65x6 mm, 3 M lomg supports 0.6 M bent outwards at top | No. | 1 | 1230.5239
& to contain 3 strands of barbed wire 0.4 mtr. sagged and concreted in ground and 2 mtr.
Vertical for gauge fencing.(3.6*6.8)*Rs.51+((3.6*6.8)*Rs.51)*0%=979
2 | Supports required at every 2 mtr. For 127 mtr. Periphery of switchyard 64 nos. | No. | 1 | 1109.76
(3.2*6.8)*Rs.51+((3.2*6.8)*Rs.51)*0%
Rates on HPSSR 2009
1 | P/LCC 1:4:8 (1 cement 4 sand 8 graded stone aggregate 40mm normal size ) in foundation/pludg | cmt |  | 2452
item 09130000 P151
2 | P/LCC 1:5:10 (1 cement 5 sand 10 graded stone aggregate 40mm normal size ) in foundation/pludg | cmt |  | 2208
item 09150000 P151
3 | P/LCC 1:2:4 (1 cement 2 sand 10 graded stone aggregate 40mm normal size )in foundation/pludg | cmt |  | 3386
item 0920010 P152
4 | RCC 1:2:4(1 cement 2 sand 10 graded stone aggregate 40mm normal size ) in foundation/pludg | cmt |  | 8002
item 09380100 P157
5 | 1st class brick Masonry 1:6
| item 010010901 P165 | cmt |  | 3116
6 | 10MM cement Plaster 1:6
| item 17046040 P345 | cmt |  | 57.7
7 | Trench O B (TYPE) | cmt |  | 1053
8 | Trench O C (TYPE) | cmt |  | 854
PAGE-80
ANALYSIS Page --43
A) | Expended metal fencing around switchyard
1 | M.S. angle iron 65x65x6 mm, 3 M long supports 0.6 M bent outwards at top & | No. | 1 | 1231
to contain 3 strands of barbed wire 0.4 mtr. Sagged and concreted in ground and 2 mtr.
Vertical for gauge fencing.(3.6*6.8)*Rs.51+((3.6*6.8)*Rs.51)*0%
2 | Supports required at every 2 mtr. For 127 mtr. Periphery of switchyard 64 nos. | No. | 1 | 1094
(3.2*6.8)*Rs.51+((3.2*6.8)*Rs.51)*0%
(B) | Gate at colony & switchyard entrance.
Gate cost of masonry
M.S angle iron 65x65x6mm gates, 1.5x2.5 mtr. Each grill works 2 No. I.e.
2x1.5x2.5sq. mtr. Wicket gate.
| ((8*6.8)*Rs.51+((8*6.8)*Rs.51)*0%)*2 | Sq. Mtr. | 1 | 729.2
| Gate cost of masonry | No. | 1 | 1943
((1.5*0.6)*1.21*1.1*1399)*3
| Expended metal at 10 % wastage 1.1x127x2 =279.4 say 280 Sq mtr | Sq.Mtr. |  | 613

## 11 P.O.81-89
P-81
STATEMENT SHOWING RATES OF EQUIPMENTS/MATERIAL FOR THE COST DATA 2012-13(11 kV SYSTEM)
S. | SUPPLIER | P.O.NO.& DATE | DESCRIPTION | QTY | UNIT | RATE | E.D | Edu. | SALE | F&I,UN- |  | DIS- | GRAND | UNIT | ROUNDED | ROUNDED
No. | [7 empty] | Cess | TAX/VAT | LOADING | TOTAL | -COUNT | TOTAL | RATE | RATE FOR | RATE FOR
[10 empty] | CHARGES |  |  |  |  | 2011-12 | 2012-13
with 6.95 % Hike
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
A | STEEL TUBULAR POLES :-
1 | M/S Jindal Industries Ltd. | CE(MM)-I-STP(Jindal)-TE-11/2011 | 8 MTRS | 24000 | No. | 4707.91 | 484.91 |  | 103.86 | 370.05 | 136001520 |  | 136001520 | 5666.73
I | 605, Madam Bhikaji Cama Bhawan | -32-14291-14342, Dt.15.11.11
| 11, Bhikaji Cama Place |  | Total | 24000 | [8 empty] | 136001520 | 5666.73 | 5667 | 6061
New Delhi-110066
II |  |  | 9 MTRS | 3350 | No. | 6546.66 | 674.31 |  | 144.42 | 548.5 | 26511531.5 |  | 26511531.5 | 7913.89
|  |  | Total | 3350 | [8 empty] | 26511531.5 | 7913.89 | 7914 | 8464
III |  |  | 10 MTRS | 1800 | No. | 9336.53 | 961.66 |  | 205.96 | 850.72 | 20438766 |  | 20438766 | 11354.87
|  |  | Total | 1800 | [8 empty] | 20438766 | 11354.87 | 11355 | 12144
IV |  |  | 11 MTRS | 850 | No. | 10121.36 | 1042.5 |  | 223.28 | 922.53 | 10463219.5 |  | 10463219.5 | 12309.67
|  |  | Total | 850 | [8 empty] | 10463219.5 | 12309.67 | 12310 | 13166
2 | M/S Electro Steels India | CE(MM)-II-STP-Electro Steel | 9 MTRS | 770 | No. | 6667.61 | 0 |  | 333.38 | 194.51 | 5540535 |  | 5540535 | 7195.5
I | Near Truck Union, G.T. road | -TE-23/09-L-13/10-Adll.-24651-89
| Damtal, Kangra (HP) | Dt.01.03.2011 | Total | 770 | [8 empty] | 5540535 | 7195.5 | 7196 | 7696
.
II |  |  | 10 MTRS | 182 | No. | 9793.47 | 0 |  | 489.67 | 225.15 | 1912508.78 |  | 1912508.78 | 10508.29
|  |  | Total | 182 | [8 empty] | 1912508.78 | 10508.29 | 10508 | 11238
III |  |  | 11 MTRS | 108 | No. | 10649.64 | 0 |  | 532.48 | 225.15 | 1231985.16 |  | 1231985.16 | 11407.27
|  |  | Total | 108 | [8 empty] | 1231985.16 | 11407.27 | 11407 | 12200
IV |  | CE(MM)-II-STP-Electro Steel | 9 MTRS | 850 | No. | 7417.79 | 0 |  | 296.71 | 199.39 | 6726806.5 |  | 6726806.5 | 7913.89
-TE-11/2011-L-33-14343-394
|  | Dt.15.11.2011 | Total | 850 | [8 empty] | 6726806.5 | 7913.89 | 7914 | 8464
V |  |  | 10 MTRS | 600 | No. | 10603.27 | 0 |  | 424.13 | 327.48 | 6812928 |  | 6812928 | 11354.88
|  |  | Total | 600 | [8 empty] | 6812928 | 11354.88 | 11355 | 12144
3 | M/S Frabrico (india) Pvt. Ltd | CE(MM)-II-STP/Fabrico -TE-23/09/ | 8 MTRS H/R Poles | 288 | No. | 3150 | 0 |  | 126 | 186.11 | 997087.68 |  | 997087.68 | 3462.11
I | J-1 Shastri Nagar Meerut | 10-L-12-10(ADLL)-24571-95
|  | Dt 01.03.2011. | Total | 288 | [8 empty] | 997087.68 | 3462.11 | 3462 | 3703
II |  | CE(MM)-II-STP/Fabrico -TE-11/2011 | 8 MTRS H/R Poles | 3336 | No. | 3201 | 329.7 |  | 70.61 | 298.67 | 13010333.28 |  | 13010333.28 | 3899.98
L-25-12972-13012
|  | Dt 22.10.11 | Total | 3336 | [8 empty] | 13010333.28 | 3899.98 | 3900 | 4171
4 | M/S Good Luck Steel Tubes Ltd | CE(MM)-II-STP/GoodLuck/TE-23/09 | 8 MTRS | 8169 | No. | 4283 | 441.15 |  | 236.21 | 272 | 42743148.84 |  | 42743148.84 | 5232.36
I | Good Luck House, Ambedkar Road, | -L11/10/-Adll-24596-650
| Gaziabad-201001 (UP) | Dt. 01.03.2011 | Total | 8169 | [8 empty] | 42743148.84 | 5232.36 | 5232 | 5596
P-82
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
.
II |  |  | 9 MTRS | 1796 | No. | 5892 | 606.88 |  | 324.94 | 377 | 12932672.72 |  | 12932672.72 | 7200.82
|  |  | Total | 1796 | [8 empty] | 12932672.72 | 7200.82 | 7201 | 7701
III |  |  | 10 MTRS | 424 | No. | 8614.16 | 887.26 |  | 475.07 | 541 | 4459415.76 |  | 4459415.76 | 10517.49
|  |  | Total | 424 | [8 empty] | 4459415.76 | 10517.49 | 10517 | 11248
IV |  |  | 11 MTRS | 251 | No. | 9349.31 | 962.98 |  | 515.61 | 590 | 2865892.9 |  | 2865892.9 | 11417.9
|  |  | Total | 251 | [8 empty] | 2865892.9 | 11417.9 | 11418 | 12212
| Average Rate of Steel Tubular Poles | 8 MTRS LONG | Total | 32169 | [8 empty] | 178744668.84 | 5556.426 | 5556 | 5942
|  | 9 MTRS LONG | Total | 6766 | [8 empty] | 51711545.72 | 7642.8533 | 7643 | 8174
|  | 10 MTRS LONG | Total | 3006 | [8 empty] | 33623618.54 | 11185.5018 | 11186 | 11963
|  | 11 MTRS LONG | Total | 1209 | [8 empty] | 14561097.56 | 12043.9186 | 12044 | 12881
|  | 8 MTRS LONG H/R | Total | 3624 | [8 empty] | 14007420.96 | 3865.1824 | 3865 | 4134
B | PCC Poles
5 | M/S Farm Fresh Foods Pvt. Ltd. | CE(MM)XI-PCC Poles-Farm Fresh | 8 Mtrs (W/L 200Kg) | 82 | No | 1357 |  |  | 54.28 | 310.73 | 141204.82 |  | 141204.82 | 1722.01
I | Batamandi, Poanta Sahib, | -20/09/L-08-(AO)-24773-798
| Paonta Shahib, Sirmour (HP)-173025 | Dt.03.03.11 | Total | 82 | [8 empty] | 141204.82 | 1722.01 | 1722 | 1842
II |  |  | 8 Mtrs (W/L 200Kg) | 384 | No | 1357 |  |  | 54.28 | 312.95 | 662104.32 |  | 662104.32 | 1724.23
|  |  | Total | 384 | [8 empty] | 662104.32 | 1724.23 | 1724 | 1844
III |  |  | 8 Mtrs Jtd. (W/L150Kg) | 236 | No | 1546 |  |  | 61.84 | 364.21 | 465403.8 |  | 465403.8 | 1972.05
|  |  | Total | 236 | [8 empty] | 465403.8 | 1972.05 | 1972 | 2109
IV |  |  | 8 Mtrs Jtd. (W/L150Kg) | 20 | No | 1546 |  |  | 61.84 | 352.92 | 39215.2 |  | 39215.2 | 1960.76
|  |  | Total | 20 | [8 empty] | 39215.2 | 1960.76 | 1961 | 2097
V |  | CE(MM)-XI-PCC Poles-Farm Fresh | 8 Mtrs (W/L 200Kg) | 506 | No | 1505 |  |  | 75.25 | 206.67 | 904181.52 |  | 904181.52 | 1786.92
-09/2011-L-21-11760-82
|  | Dt.29.09.2011 | Total | 506 | [8 empty] | 904181.52 | 1786.92 | 1787 | 1911
VI |  |  | 8 Mtrs (W/L 200Kg) | 87 | No | 1505 |  |  | 75.25 | 227.18 | 157246.41 |  | 157246.41 | 1807.43
|  |  | Total | 87 | [8 empty] | 157246.41 | 1807.43 | 1807 | 1933
VII |  |  | 8 Mtrs (W/L 200Kg) | 130 | No | 1505 |  |  | 75.25 | 227.18 | 234965.9 |  | 234965.9 | 1807.43
|  |  | Total | 130 | [8 empty] | 234965.9 | 1807.43 | 1807 | 1933
6 | M/S Kreative Concrete Industries | CE(MM)XI-PCC Poles-KCI | 9 Mtrs (W/L 180 kg) | 100 | No | 1700 |  |  | 68 | 180 | 194800 |  | 194800 | 1948
I | VPO, Lodhwan, Tehsil Nurpur | -20/09/-L-06-(AO)-24705-724
| Distt. Kangra (HP) | Dt. 03.03.2011 | Total | 100 | [8 empty] | 194800 | 1948 | 1948 | 2083
II |  |  | 9 Mtrs (W/L 180 kg) | 401 | No | 1700 |  |  | 68 | 70 | 737038 |  | 737038 | 1838
|  |  | Total | 401 | [8 empty] | 737038 | 1838 | 1838 | 1966
III |  |  | 8 Jtd. Mtrs | 192 | No | 1675 |  |  | 67 | 70 | 347904 |  | 347904 | 1812
|  |  | Total | 192 | [8 empty] | 347904 | 1812 | 1812 | 1938
P-83
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
IV |  | CE(MM)XI-PCC Poles-KCI | 9 Mtrs (W/L 180 kg) | 499 | No | 1790 |  |  | 89.5 | 80 | 977790.5 |  | 977790.5 | 1959.5
-09/2011-L-20-11783-99
|  | Dt. 29.09.2011 | Total | 499 | [8 empty] | 977790.5 | 1959.5 | 1960 | 2096
7 | M/S Deep Concrete Products | CE(MM)XI-PCC Poles-Deep | 9 Mtrs (W/L 180 kg) | 503 | No | 1750 |  |  | 70 | 100 | 965760 |  | 965760 | 1920
I | Vill. Malpur, P.O. Baddi, The. Nalagarh | -20/09/L-07-(AO)-24725-45
| Distt. Solan(HP)-173205 | Dt. 03.03.2011 | Total | 503 | [8 empty] | 965760 | 1920 | 1920 | 2053
II |  | CE(MM)-XI-PCC Poles-Deep | 8 Mtrs (W/L 200Kg) | 108 | No | 1415 |  |  | 70.75 | 200 | 182061 |  | 182061 | 1685.75
,-09/2011-L-18-11695-11742
|  | Dt. 29.09.2011 | Total | 108 | [8 empty] | 182061 | 1685.75 | 1686 | 1803
III |  |  | 8 Mtrs (W/L 200Kg) | 206 | No | 1415 |  |  | 70.75 | 170 | 341084.5 |  | 341084.5 | 1655.75
|  |  | Total | 206 | [8 empty] | 341084.5 | 1655.75 | 1656 | 1771
IV |  |  | 8 Mtrs (W/L 200Kg) | 250 | No | 1415 |  |  | 70.75 | 70 | 388937.5 |  | 388937.5 | 1555.75
|  |  | Total | 250 | [8 empty] | 388937.5 | 1555.75 | 1556 | 1664
V |  |  | 8 Mtrs (W/L 200Kg) | 426 | No | 1415 |  |  | 70.75 | 140 | 692569.5 |  | 692569.5 | 1625.75
|  |  | Total | 426 | [8 empty] | 692569.5 | 1625.75 | 1626 | 1739
VI |  |  | 8 Mtrs (W/L 200Kg) | 487 | No | 1415 |  |  | 70.75 | 200 | 820960.25 |  | 820960.25 | 1685.75
|  |  | Total | 487 | [8 empty] | 820960.25 | 1685.75 | 1686 | 1803
VII |  |  | 8 Mtrs (W/L 200Kg) | 603 | No | 1415 |  |  | 70.75 | 200 | 1016507.25 |  | 1016507.25 | 1685.75
|  |  | Total | 603 | [8 empty] | 1016507.25 | 1685.75 | 1686 | 1803
VIII |  |  | 8 Mtrs (W/L 200Kg) | 1113 | No | 1415 |  |  | 70.75 | 90 | 1753809.75 |  | 1753809.75 | 1575.75
|  |  | Total | 1113 | [8 empty] | 1753809.75 | 1575.75 | 1576 | 1686
IX |  |  | 8 Mtrs (W/L 200Kg) | 80 | No | 1415 |  |  | 70.75 | 140 | 130060 |  | 130060 | 1625.75
|  |  | Total | 80 | [8 empty] | 130060 | 1625.75 | 1626 | 1739
X |  |  | 9 Mtrs (W/L 180 kg) | 760 | No | 1715 |  |  | 85.75 | 250 | 1558570 |  | 1558570 | 2050.75
|  |  | Total | 760 | [8 empty] | 1558570 | 2050.75 | 2051 | 2194
XI |  |  | 9 Mtrs (W/L 180 kg) | 104 | No | 1715 |  |  | 85.75 | 150 | 202878 |  | 202878 | 1950.75
|  |  | Total | 104 | [8 empty] | 202878 | 1950.75 | 1951 | 2087
XII |  |  | 9 Mtrs (W/L 180 kg) | 928 | No | 1715 |  |  | 85.75 | 100 | 1763896 |  | 1763896 | 1900.75
|  |  | Total | 928 | [8 empty] | 1763896 | 1900.75 | 1901 | 2033
XII |  |  | 9 Mtrs (W/L 180 kg) | 326 | No | 1715 |  |  | 85.75 | 230 | 662024.5 |  | 662024.5 | 2030.75
|  |  | Total | 326 | [8 empty] | 662024.5 | 2030.75 | 2031 | 2172
XIII |  |  | 9 Mtrs (W/L 180 kg) | 50 | No | 1715 |  |  | 85.75 | 100 | 95037.5 |  | 95037.5 | 1900.75
|  |  | Total | 50 | [8 empty] | 95037.5 | 1900.75 | 1901 | 2033
P-84
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
XIV |  |  | 9 Mtrs (W/L 180 kg) | 314 | No | 1715 |  |  | 85.75 | 280 | 653355.5 |  | 653355.5 | 2080.75
|  |  | Total | 314 | [8 empty] | 653355.5 | 2080.75 | 2081 | 2226
XV |  |  | 9.75 Mtrs (W/L 173 kg) | 230 | No | 2275 |  |  | 113.75 | 200 | 595412.5 |  | 595412.5 | 2588.75
|  |  | Total | 230 | [8 empty] | 595412.5 | 2588.75 | 2589 | 2769
XVI |  |  | 9.75 Mtrs (W/L 173 kg) | 100 | No | 2275 |  |  | 113.75 | 170 | 255875 |  | 255875 | 2558.75
|  |  | Total | 100 | [8 empty] | 255875 | 2558.75 | 2559 | 2737
8 | M/S K.B. Industries | CE(MM)XI-PCC Poles-KBI | 8 Mtrs | 666 | No | 1439 |  |  | 57.56 | 150 | 1096608.96 |  | 1096608.96 | 1646.56
I | Vill. Chachelli, Ind. Area | -20/09/L-09 (AO)-24746-772
| Defence Road, P.O. Sujanpur | Dt. 03.03.2011 | Total | 666 | [8 empty] | 1096608.96 | 1646.56 | 1647 | 1761
(PB)-145023
II |  |  | 8 Mtrs | 382 | No | 1439 |  |  | 57.56 | 79 | 601863.92 |  | 601863.92 | 1575.56
|  |  | Total | 382 | [8 empty] | 601863.92 | 1575.56 | 1576 | 1686
III |  |  | 8 Mtrs | 666 | No | 1439 |  |  | 57.56 | 60 | 1036668.96 |  | 1036668.96 | 1556.56
|  |  | Total | 666 | [8 empty] | 1036668.96 | 1556.56 | 1557 | 1665
IV |  |  | 8 Mtrs | 444 | No | 1439 |  |  | 57.56 | 210 | 757712.64 |  | 757712.64 | 1706.56
|  |  | Total | 444 | [8 empty] | 757712.64 | 1706.56 | 1707 | 1826
|  | CE(MM)XI-PCC Poles-KBI | 8 Mtrs | 1257 | No | 1455 |  |  | 72.75 | 65 | 2002086.75 |  | 2002086.75 | 1592.75
V |  | -09/2011-L-19-11743-59
|  | Dt. 29.09.2011 | Total | 1257 | [8 empty] | 2002086.75 | 1592.75 | 1593 | 1704
9 | M/S Himachal Concrete Cor[oration | CE(MM)XI-PCC Poles-HCC | 8 Jtd. Mtrs | 16 | No | 1753 |  |  | 70.12 | 125 | 31169.92 |  | 31169.92 | 1948.12
I | Kansa Chowk, PO Dhaban | -20/09/L-05-(AO)-24799-828
| Distt. Mandi (HP)-175027 | Dt. 03.03.2011 | Total | 16 | [8 empty] | 31169.92 | 1948.12 | 1948 | 2083
II |  |  | 8 Jtd. Mtrs | 100 | No | 1753 |  |  | 70.12 | 125 | 194812 |  | 194812 | 1948.12
|  |  | Total | 100 | [8 empty] | 194812 | 1948.12 | 1948 | 2083
III |  |  | 9 Jtd. Mtrs | 124 | No | 2140 |  |  | 85.6 | 525 | 341074.4 |  | 341074.4 | 2750.6
|  |  | Total | 124 | [8 empty] | 341074.4 | 2750.6 | 2751 | 2942
IV |  |  | 9 Jtd. Mtrs | 40 | No | 2400 |  |  | 96 | 300 | 111840 |  | 111840 | 2796
|  |  | Total | 40 | [8 empty] | 111840 | 2796 | 2796 | 2990
| Average Rate of PCC Poles | 8 MTRS LONG | Total | 7877 | [8 empty] | 12920633.95 | 1640.2988 | 1640 | 1754
|  | 8 MTRS LONG (JTD.) | Total | 564 | [8 empty] | 1078504.92 | 1912.2428 | 1912 | 2045
|  | 9 MTRS LONG | Total | 3985 | [8 empty] | 7811150 | 1960.138 | 1960 | 2096
|  | 9 MTRS LONG (JTD.) | Total | 164 | [8 empty] | 452914.4 | 2761.6732 | 2762 | 2954
|  | 9.75 MTRS LONG | Total | 330 | [8 empty] | 851287.5 | 2579.6591 | 2580 | 2759
P-85
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
C | CONDUCTORS
10 | M/S Durable Conductor | CE (MM) /IV/2577(A)/910/ACSR | ACSR 6/1/3.35mm. | 323.9 | Km | 23585.78 | 0 |  | 1204.29 | 742 | 8269837.473 |  | 8269837.473 | 25532.07
I | HO Santushti Old Power Road | AAAC/-23-69 Dt. 01.04.12
| Solan (HP) |  | Total | 323.9 | [8 empty] | 8269837.473 | 25532.07 | 25532 | 27306
II |  |  | AAAC 7/2.00 mm | 208.4 | Km | 8625.61 | 0 |  | 442.28 | 328 | 1958103.476 |  | 1958103.476 | 9395.89
|  |  | Total | 208.4 | [8 empty] | 1958103.476 | 9395.89 | 9396 | 10049
III |  |  | AAAC 7/2.50 mm | 598.8 | Km | 13428.5 | 0 |  | 686.42 | 435 | 8712492.096 |  | 8712492.096 | 14549.92
|  |  | Total | 598.8 | [8 empty] | 8712492.096 | 14549.92 | 14550 | 15561
IV |  |  | AAAC 7/3.15 mm | 863.7 | Km | 21226.83 | 0 |  | 1083.84 | 670 | 19848404.679 |  | 19848404.679 | 22980.67
|  |  | Total | 863.7 | [8 empty] | 19848404.679 | 22980.67 | 22981 | 24578
11 | M/s NU-Line Industries Pvt. Ltd. | CE (MM) /IV/2576(A)/910/ACSR/ | ACSR 6/1/2.59mm. | 400.3 | Km | 14482.1 | 0 |  | 738.11 | 409.5 | 6256572.913 |  | 6256572.913 | 15629.71
I | 36/37, Industrial Area, | AAAC/ -70-116 Dated 01.04.2011
| Sector-1, Parwanoo |  | Total | 400.3 | [8 empty] | 6256572.913 | 15629.71 | 15630 | 16716
Distt Solan(HP)
II |  |  | AAC 7/3.10 mm | 61.2 | Km | 20079 | 0 |  | 1023.95 | 535 | 1324242.54 |  | 1324242.54 | 21637.95
|  |  | Total | 61.2 | [8 empty] | 1324242.54 | 21637.95 | 21638 | 23142
III |  |  | AAAC 7/3.81mm | 526 | Km | 30802.35 | 0 |  | 1555.12 | 580 | 17325109.22 |  | 17325109.22 | 32937.47
|  |  | Total | 526 | [8 empty] | 17325109.22 | 32937.47 | 32937 | 35226
IV |  |  | AAAC 7/4.26 mm | 327.2 | Km | 38800 | 0 |  | 1975 | 1100 | 13701500 |  | 13701500 | 41875
|  |  | Total | 327.2 | [8 empty] | 13701500 | 41875 | 41875 | 44785
V |  | CE (MM) /IV/2576(A)/910/ACSR/ | ACSR 6/1/4.72mm. | 120 | Km | 47958.1 | 0 |  | 2446.9 | 1395 | 6216000 |  | 6216000 | 51800
AAAC/ -07-22 Dated 01.04.2011
|  |  | Total | 120 | [8 empty] | 6216000 | 51800 | 51800 | 55400
| Average Rate of Conductors | ACSR 6/1/2.11 mm | Total
|  | ACSR 6/1/2.59mm. | Total | 400.3 | [8 empty] | 6256572.913 | 15629.71 | 15630 | 16716
|  | ACSR 6/1/3.35mm. | Total | 323.9 | [8 empty] | 8269837.473 | 25532.07 | 25532 | 27306
|  | ACSR 6/1/4.72mm | Total | 120 | [8 empty] | 6216000 | 51800 | 51800 | 55400
|  | AAAC 7/2.00 mm | Total | 208.4 | [8 empty] | 1958103.476 | 9395.89 | 9396 | 10049
|  | AAAC 7/2.50 mm | Total | 598.8 | [8 empty] | 8712492.096 | 14549.92 | 14550 | 15561
|  | AAAC 7/3.15 mm | Total | 863.7 | [8 empty] | 19848404.679 | 22980.67 | 22981 | 24578
|  | AAAC 7/3.81 mm | Total | 526 | [8 empty] | 17325109.22 | 32937.47 | 32937 | 35226
|  | AAAC 7/4.26 mm | Total | 327.2 | [8 empty] | 13701500 | 41875 | 41875 | 44785
|  | AAC 7/3.10 mm | Total | 61.2 | [8 empty] | 1324242.54 | 21637.95 | 21638 | 23142
D | G.I. WIRE/BARBED WIRE/STAY WIRE
GI Wire
12 | M/S Bajrang Wire Products(India) (P) Ltd. | CE (MM)/IV:-GMS-07/2011)-L-15 | ISS 280/1978 & ISS 4826/19379(2001-06) GI wire
I | E-762(A), Road No. 9F-1 V. K.I Area | 9092-9144 Dt. 30.08.11 | 6 SWG 5.0 mm | 23.83 | MT | 46000 |  |  | 7305.34 | 1638.63 | 1309314.8051 |  | 1309314.8051 | 54943.97
Jaipur-302013, Rajsthan, India
|  |  | Total | 23.83 | [8 empty] | 1309314.8051 | 54943.97 | 54944 | 58763
P-86
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
II |  |  | 8 SWG 4.0 mm | 119.4 | MT | 46250 |  |  | 7345.05 | 1638.7 | 6594909.75 |  | 6594909.75 | 55233.75
|  |  | Total | 119.4 | [8 empty] | 6594909.75 | 55233.75 | 55234 | 59073
III |  |  | 10 SWG 3.15 mm | 32.7 | MT | 46750 |  |  | 7424.46 | 1638.7 | 1825090.332 |  | 1825090.332 | 55813.16
|  |  | Total | 32.7 | [8 empty] | 1825090.332 | 55813.16 | 55813 | 59692
IV |  | CE (MM)/IV:-GMS-(AO)-07/2011 | ISS 280/1978 & ISS 4826/19379(2001-06) GI wire
|  | L-24128-49 Dt. 27.02.12 | 6 SWG 5.0 mm | 9.532 | MT | 46000 |  |  | 7305.34 | 1638.63 | 523725.922 |  | 523725.922 | 54943.97
|  |  | Total | 9.532 | [8 empty] | 523725.922 | 54943.97 | 54944 | 58763
V |  |  | 8 SWG 4.0 mm | 47.76 | MT | 46250 |  |  | 7345.05 | 1638.7 | 2637963.9 |  | 2637963.9 | 55233.75
|  |  | Total | 47.76 | [8 empty] | 2637963.9 | 55233.75 | 55234 | 59073
VI |  |  | 10 SWG 3.15 mm | 13.08 | MT | 46750 |  |  | 7424.46 | 1638.7 | 730036.1328 |  | 730036.1328 | 55813.16
|  |  | Total | 13.08 | [8 empty] | 730036.1328 | 55813.16 | 55813 | 59692
13 | M/S Himachal Wire Industries (P) Ltd. | CE (MM)/IV:-GMS-07/2011)-L-16 | ISS 280/1978 & ISS 4826/19379(2001-06) GI wire
I | G.T. Road, Damtal Distt. Kangra (HP) | 9145-65 Dt. 30.08.11 | 6 SWG 5.0 mm | 10.21 | MT | 52079.97 |  |  | 2614 | 250 | 560977.9337 |  | 560977.9337 | 54943.97
|  |  | Total | 10.21 | [8 empty] | 560977.9337 | 54943.97 | 54944 | 58763
II |  |  | 8 SWG 4.0 mm | 51.17 | MT | 52355.95 |  |  | 2627.8 | 250 | 2826310.9875 |  | 2826310.9875 | 55233.75
|  |  | Total | 51.17 | [8 empty] | 2826310.9875 | 55233.75 | 55234 | 59073
III |  |  | 10 SWG 3.15 mm | 14 | MT | 52907.76 |  |  | 2655.39 | 250 | 781384.1 |  | 781384.1 | 55813.15
|  |  | Total | 14 | [8 empty] | 781384.1 | 55813.15 | 55813 | 59692
IV |  | CE (MM)/IV:-GMS-(AO)-07/2011) | ISS 280/1978 & ISS 4826/19379(2001-06) GI wire
|  | 24150-82 Dt. 27.02.12 | 6 SWG 5.0 mm | 4.08 | MT | 52079.97 |  |  | 2614 | 250 | 224171.3976 |  | 224171.3976 | 54943.97
|  |  | Total | 4.08 | [8 empty] | 224171.3976 | 54943.97 | 54944 | 58763
V |  |  | 8 SWG 4.0 mm | 20.46 | MT | 52355.95 |  |  | 2627.8 | 250 | 1130082.525 |  | 1130082.525 | 55233.75
|  |  | Total | 20.46 | [8 empty] | 1130082.525 | 55233.75 | 55234 | 59073
VI |  |  | 10 SWG 3.15 mm | 5.6 | MT | 52907.76 |  |  | 2655.39 | 250 | 312553.64 |  | 312553.64 | 55813.15
|  |  | Total | 5.6 | [8 empty] | 312553.64 | 55813.15 | 55813 | 59692
| Average Rate of GI wire | GI Wire | 6 SWG | 47.652 | [8 empty] | 2618190.0584 | 54943.97 | 54944 | 58763
|  |  | 8SWG | 238.79 | [8 empty] | 13189267.1625 | 55233.75 | 55234 | 59073
|  |  | 10 SWG | 65.38 | [8 empty] | 3649064.2048 | 55813.157 | 55813 | 59692
Stay Wire
14 | M/S Himachal Wire Industries (P) Ltd. | CE (MM)/IV:GSS-17/2010 | ISS 2141/1992/2006 & 4826/1979(2001-06)
I | G.T. Road, Damtal Distt. Kangra (HP) | -L-42- 27665-710 | 7/4.00 mm | 134.27 | MT | 50000 |  |  | 2510 | 250 | 7084085.2 |  | 7084085.2 | 52760
dt. 26.03.11
|  |  | Total | 134.27 | [8 empty] | 7084085.2 | 52760 | 52760 | 56427
II |  |  | 7/3.15 mm | 135.03 | MT | 51000 |  |  | 2560 | 250 | 7265964.3 |  | 7265964.3 | 53810
|  |  | Total | 135.03 | [8 empty] | 7265964.3 | 53810 | 53810 | 57550
P-87
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
III |  | CE (MM)/IV:GSS-10/2011 | ISS 2141/1992/2006 & 4826/1979(2001-06)
|  | -L-13- 8017-8066 | 7/4.00 mm | 84.831 | MT | 53460 |  |  | 2146.4 | 250 | 4738354.2684 |  | 4738354.2684 | 55856.4
dt. 16.08.2011
|  |  | Total | 84.831 | [8 empty] | 4738354.2684 | 55856.4 | 55856 | 59738
IV |  |  | 7/3.15 mm | 129.671 | MT | 54450 |  |  | 2186 | 250 | 7376464.506 |  | 7376464.506 | 56886
|  |  | Total | 129.671 | [8 empty] | 7376464.506 | 56886 | 56886 | 60840
V |  | CE (MM)/IV:GSS-17/2010 | ISS 2141/1992/2006 & 4826/1979(2001-06)
|  | -L-42 (AO)- 10353-385 | 7/4.00 mm | 53.708 | MT | 50000 |  |  | 2510 | 250 | 2833634.08 |  | 2833634.08 | 52760
dt. 14.9.11
|  |  | Total | 53.708 | [8 empty] | 2833634.08 | 52760 | 52760 | 56427
VI |  |  | 7/3.15 mm | 54.014 | MT | 51000 |  |  | 2560 | 250 | 2906493.34 |  | 2906493.34 | 53810
|  |  | Total | 54.014 | [8 empty] | 2906493.34 | 53810 | 53810 | 57550
VII |  | CE (MM)/IV:GSS-10/2011 (AO) | ISS 2141/1992/2006 & 4826/1979(2001-06)
|  | -L-16- 23460-91 | 7/4.00 mm | 33.93 | MT | 53460 |  |  | 2146.4 | 250 | 1895207.652 |  | 1895207.652 | 55856.4
dt. 14.02.2012
|  |  | Total | 33.93 | [8 empty] | 1895207.652 | 55856.4 | 55856 | 59738
VII |  |  | 7/3.15 mm | 40.2 | MT | 54450 |  |  | 2186 | 250 | 2286817.2 |  | 2286817.2 | 56886
|  |  | Total | 40.2 | [8 empty] | 2286817.2 | 56886 | 56886 | 60840
| Average Rate of Stay Wire | Stay Wire | 7/4.00 mm | 306.739 | [8 empty] | 16551281.2004 | 53958.8419 | 53959 | 57709
|  |  | 7/3.15 mm | 358.915 | [8 empty] | 19835739.346 | 55265.8411 | 55266 | 59107
Barbed Wire
15 | M/s Apple Weldmes Industries | CE(MM)/IV-Barbed wire-/2009- | IS 4826/1979(2001-06) | 21.2 | MT | 48000 |  |  | 6600 |  | 1157520 |  | 1157520 | 54600
I | The Mall, Solan. | L-22434-67 dated 02.02.2011.
|  |  | Total | 21.2 | [8 empty] | 1157520 | 54600 | 54600 | 58395
16 | M/s Brijsons Hetreat, VPO Bhadroya | CE(MM)/IV-Barbed wire-/2009- | IS 4826/1979(2001-06) | 23.79 | MT | 48000 |  |  | 6600 |  | 1298934 |  | 1298934 | 54600
I | The. Nurpur, Distt. Kangra. | L-23145-78 dated 07.02.2011.
|  |  | Total | 23.79 | [8 empty] | 1298934 | 54600 | 54600 | 58395
| Average Rate of Barbed Wire | Barbed Wire | Total | 44.99 | [8 empty] | 2456454 | 54600 | 54600 | 58395
E | PVC TWIN CORE
17 | M/s Shaan Aluminium Company, | CE(MM)/XII:PVCTC-13/2010-L-15(A) | 2Cx6 mm2 | 922 | Kms. | 6270 | 0 |  | 361 | 1095 | 7123372 |  | 7123372 | 7726
I | Village Kamli, Parwanoo, | 2429-82 Dt.07.05.2011
| District Solan (HP) |  | Total | 922 | [8 empty] | 7123372 | 7726 | 7726 | 8263
II |  |  | 2Cx16 mm2 | 128.8 | Kms. | 14800 | 0 |  | 860 | 2750 | 2371208 |  | 2371208 | 18410
|  |  | Total | 128.8 | [8 empty] | 2371208 | 18410 | 18410 | 19689
18 | M/s Preeti Industries | CE(MM)/XII:PVCTC-13/2010-L-14(A) | 2Cx10 mm2 | 425.5 | Kms. | 9775 | 0 |  | 560 | 1727 | 5132381 |  | 5132381 | 12062
I | Village Kamli, Parwanoo, | 2378-2428 Dt. 07.05.2012
| District Solan (HP) |  | Total | 425.5 | [8 empty] | 5132381 | 12062 | 12062 | 12900
II |  |  | 2Cx25mm2 | 61.3 | Kms. | 21250 | 0 |  | 1220 | 3713 | 1605017.9 |  | 1605017.9 | 26183
|  |  | Total | 61.3 | [8 empty] | 1605017.9 | 26183 | 26183 | 28003
P-88
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
19 | M/s Himachal Aluminium & Conductors | CE(MM)/XII/TE-5/2011-5634-53 | 2Cx6 mm2 | 30 | Kms. | 7761 | 0 |  | 390.55 | 170 | 249646.5 |  | 249646.5 | 8321.55
I | GT Road, VPO Mohtli | Dated 07.07.11
| Distt. Kangra (HP) |  | Total | 30 | [8 empty] | 249646.5 | 8321.55 | 8322 | 8900
II |  |  | 2Cx10 mm2 | 105 | Kms. | 11940 | 0 |  | 600.75 | 300 | 1348278.75 |  | 1348278.75 | 12840.75
|  |  | Total | 105 | [8 empty] | 1348278.75 | 12840.75 | 12841 | 13733
III |  |  | 2Cx16 mm2 | 15 | Kms. | 17910 | 0 |  | 903 | 500 | 289695 |  | 289695 | 19313
|  |  | Total | 15 | [8 empty] | 289695 | 19313 | 19313 | 20655
| Average Rate of Twin Core PVC | PVC 2x6mm2 | Total | 952 | [8 empty] | 7373018.5 | 7744.7673 | 7745 | 8283
|  | PVC 2x10mm2 | Total | 530.5 | [8 empty] | 6480659.75 | 12216.1352 | 12216 | 13065
|  | PVC 2x16mm2 | Total | 143.8 | [8 empty] | 2660903 | 18504.1933 | 18504 | 19790
|  | PVC 2x25mm2 | Total | 61.3 | [8 empty] | 1605017.9 | 26183 | 26183 | 28003
F | PIN/DISC INSULATORS
20 | M/s Madhav Ceramics, B-283, derawal | CE(MM)/IV- TE-06/2010-INS-L-25 | 11 kV Pin Insulator with Pin | 31734 | Nos. | 73.81 |  |  | 3.69 | 9.5 | 2760858 |  | 2760858 | 87
I | Nagar, Model Town, Delhi-9. | 18013-62 Dt. 10.12.2010.
|  |  | Total | 31734 | [8 empty] | 2760858 | 87 | 87 | 93
21 | M/s Garg Insulator (P) Ltd. C/O | CE(MM)/IV- TE-06/2010-INS-L-24 | 22 kV Pin Insulator with Pin | 7224 | Nos. | 210.48 |  |  | 10.52 | 15 | 1704864 |  | 1704864 | 236
I | Garg Cotton & Genral Mills, Ist | 17963-18012 Dt. 10.12.2010.
| Industrial Area, Sirsa Haryana |  | Total | 7224 | [8 empty] | 1704864 | 236 | 236 | 252
II |  |  | 33 kV Pin Insulator with Pin | 857 | Nos. | 318.55 |  |  | 15.93 | 24.5 | 307645.86 |  | 307645.86 | 358.98
|  |  | Total | 857 | [8 empty] | 307645.86 | 358.98 | 359 | 384
III |  |  | LT Shackle insulators 75x90 mm | 65073 | No. | 6.89 |  |  | 0.34 | 1 | 535550.79 |  | 535550.79 | 8.23
|  |  | Total | 65073 | [8 empty] | 535550.79 | 8.23 | 8 | 9
IV |  |  | LT Shackle insulators 115x100 mm | 3493 | No. | 14.96 |  |  | 0.75 | 2 | 61861.03 |  | 61861.03 | 17.71
|  |  | Total | 3493 | [8 empty] | 61861.03 | 17.71 | 18 | 19
22 | M/s Aggarwal Porcelain, Plot No.-69 | CE(MM)/IV- TE-06/2010-INS-L-26 | 11 kV Disc. Insulator 45 KN (B&S) | 28355 | Nos. | 153 |  |  | 7.65 | 21.6 | 5167698.75 |  | 5167698.75 | 182.25
I | Road No.-7, Industrial Area, Rani Bazar | 18063-18112 Dt. 10.12.2010.
| Bikaner-334001 |  | Total | 28355 | [8 empty] | 5167698.75 | 182.25 | 182 | 195
II |  |  | 11 kV Disc. Insulator 90 KN (B&S) | 982 | Nos. | 243 |  |  | 12.15 | 27 | 277071.3 |  | 277071.3 | 282.15
|  |  | Total | 982 | [8 empty] | 277071.3 | 282.15 | 282 | 302
III |  |  | HT Guy insulators 140x85 mm | 17332 | No. | 16 |  |  | 0.8 | 5.96 | 394476.32 |  | 394476.32 | 22.76
|  |  | Total | 17332 | [8 empty] | 394476.32 | 22.76 | 23 | 25
IV |  |  | LT Guy insulators 110x75 mm | 13212 | No. | 9.15 |  |  | 0.45 | 3.9 | 178362 |  | 178362 | 13.5
|  |  | Total | 13212 | [8 empty] | 178362 | 13.5 | 14 | 15
| Average Rate of Pin Insulators | 11 kV Pin Insulator with Pin | Total | 31734 | [8 empty] | 2760858 | 87 | 87 | 93
| , Guy Insulator, Sackle insulator | 22 kV Pin Insulator with Pin | Total | 7224 | [8 empty] | 1704864 | 236 | 236 | 252
| Disc Insulator | 33 kV Pin Insulator with Pin | Total | 857 | [8 empty] | 307645.86 | 358.98 | 359 | 384
|  | 11 kV Disc Insulator 45 KN | Total | 28355 | [8 empty] | 5167698.75 | 182.25 | 182 | 195
|  | 11 kV Disc Insulator 90KN | Total | 982 | [8 empty] | 277071.3 | 282.15 | 282 | 302
|  | LT 75X90 mm Sackle Insulator | Total | 65073 | [8 empty] | 535550.79 | 8.23 | 8 | 9
P-89
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
| Average Rate of Pin Insulators | LT 115X100mm Sackle Insulator | Total | 3493 | [8 empty] | 61861.03 | 17.71 | 18 | 19
| , Guy Insulator, Sackle insulator | HT 140x85 MM Guy Insulator | Total | 17332 | [8 empty] | 394476.32 | 22.76 | 23 | 25
| Disc Insulator | LT 110x75MM Guy Insulator | Total | 13212 | [8 empty] | 178362 | 13.5 | 14 | 15
G | LIGHTENING ARRESTOR (LA's)
23 | M/s Star Industries, 75, Link Road | CE(MM)-1/2010-LA-2010-L-16 | 9 kV, 5 KA Metal Oxide 11 kV | 1618 | No. | 299.25 |  |  | 2.99 | 21.18 | 523293.56 |  | 523293.56 | 323.42
I | Opp. New Grain Mandi, Sansar Chandra | 23223-63 Dt. 07.02.2011
| Road, jaipur-302001 (Raj.) |  | Total | 1618 | [8 empty] | 523293.56 | 323.42 | 323 | 345
II |  |  | 18 kV, 5 KA Metal Oxide 22kV | 328 | No. | 579.5 |  |  | 5.79 | 32.49 | 202631.84 |  | 202631.84 | 617.78
|  |  | Total | 328 | [8 empty] | 202631.84 | 617.78 | 618 | 661
| Average Rate of L A | 9 kV,5 KA, 11 kV Metal Oxide | Total | 1618 | [8 empty] | 523293.56 | 323.42 | 323 | 345
|  | 18 kV,5 KA, 22kV Metal Oxide | Total | 328 | [8 empty] | 202631.84 | 617.78 | 618 | 661
H | G. O. SWITCH
24 | M/s Govind Wires | CE(MM)-II-GOS-GOV-2/2010-L-20 | 11 kV, 400 A, Triple Pole, | 1359 | No. | 3686 |  |  | 184.3 | 272 | 5629385.7 |  | 5629385.7 | 4142.3
I | Plot No. 5-B Industrial area | -13900-965 dated 28.10.10 | Gang Operated, Outdoor Type
| Mehatpur Distt. Una (HP)-174315 |  | Single Throw, Single Break
II |  |  | 22 kV, 400 A, Triple Pole, | 586 | No. | 5415 |  |  | 270.75 | 584 | 3674073.5 |  | 3674073.5 | 6269.75
Gang Operated, Outdoor Type
Single Throw, Single Break
| Average Rate of GO Switch | 11 kV GO Switch | Total | 1359 | [8 empty] | 5629385.7 | 4142.3 | 4142 | 4430
|  | 22 kV GO Switch | Total | 586 | [8 empty] | 3674073.5 | 6269.75 | 6270 | 6706
25 | 11 kV 3 Core XLPE Cable | As per Rates approved by Management
|  | for spot procurment of XLPE Cables | 3x95 MM2 | 1.45 | Kms. | 651360 |  |  |  |  | 944472 |  | 944472 | 651360
dated 03.09.10
|  |  | Total | 1.45 | [8 empty] | 944472 | 651360 | 651360 | 696630
|  |  | 3x185 MM2 | 1.14 | Kms. | 901830 |  |  |  |  | 1028086.2 |  | 1028086.2 | 901830
|  |  | Total | 1.14 | [8 empty] | 1028086.2 | 901830 | 901830 | 964507
|  |  | 3x300 MM2 | 2.21 | Kms. | 1251028 |  |  |  |  | 2764771.88 |  | 2764771.88 | 1251028
|  |  | Total | 2.21 | [8 empty] | 2764771.88 | 1251028 | 1251028 | 1337974
|  |  | 3x400 MM2 | 0.15 | Kms. | 1625134 |  |  |  |  | 243770.1 |  | 243770.1 | 1625134
|  |  | Total | 0.15 | [8 empty] | 243770.1 | 1625134 | 1625134 | 1738081
| Average Rate of 3.5 core XLPE Cable | 3x95 MM2 | Total | 1.45 | [8 empty] | 944472 | 651360 | 651360 | 696630
|  | 3x185 MM2 | Total | 1.14 | [8 empty] | 1028086.2 | 901830 | 901830 | 964507
|  | 3x300 MM2 | Total | 2.21 | [8 empty] | 2764771.88 | 1251028 | 1251028 | 1337974
|  | 3x400 MM2 | Total | 0.15 | [8 empty] | 243770.1 | 1625134 | 1625134 | 1738081

## 33 PO 90-94
P-90
STATEMENT SHOWING RATES OF EQUIPMENTS/MATERIAL FOR THE COST DATA 2012-13 (33 kV SYSTEM)
S. | SUPPLIER | P.O.NO. & DATE | DESCRIPTION | QTY | UNIT | RATE | E.D | Edu. | SALE | F&I,UN- |  | DIS- | GRAND | UNIT | ROUNDED | ROUNDED
NO | [7 empty] | Cess | TAX/VAT | LOADING | TOTAL | COUNT | TOTAL | RATE | RATE FOR | RATE FOR
[10 empty] | CHARGES |  |  |  |  | 2011-12 | 2012-13
with 6.95% Hike
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
A | CURRENT AND POTENTIAL TRANSFORMERS: |  | 11 kV/110 V CT-PT Combined Unit Outdoor, Oil Imersed, Class .5 Consisting of Three CT on R,Y and B & 1 No. 11 kV/110 V PT Class .5
1 | M/S Avon Industries | CE(MM)/VII: CT-PT/2009(A)-L-18 | 15/5 A | 20 | Nos
| D-16 Industrial Focal Point | 4577-95 Dt. 14.06.2010 | 20/5 A | 10 | Nos
| Dera Bassi(Pb) |  | 25/5 A | 19 | Nos
I |  |  | 50/5 A | 10 | Nos
|  |  | 300/5 A | 1 | Nos
|  |  | Total | 60 |  | 19443.91 | 1602.18 |  | 2630.76 | 509.91 | 24186.76 |  | 1451205.6 | 24186.76
|  |  | Total | 60 |  | 19443.91 | [6 empty] | 1451205.6 | 24186.76 | 24187 | 25868
II |  |  | 22 kV/110 V CT-PT Combined Unit Outdoor, Oil Imersed, Class .5 Consisting of Three CT on R,Y and B & 1 No. 22 kV/110 V PT Class .5
|  | i) | 25/5 A | 1 | Nos
|  |  | Total | 1 |  | 30509.88 | 2514.01 |  | 4127.99 | 511.87 | 37663.75 |  | 37663.75 | 37663.75
|  |  | Total | 1 |  | 30509.88 | [6 empty] | 37663.75 | 37663.75 | 37664 | 40282
III |  |  | 33 kV/110 V CT-PT Combined Unit Outdoor, Oil Imersed, Class .5 Consisting of Three CT on R,Y and B & 1 No. 33 kV/110 V PT Class .5
|  | i) | 50/1 A | 1 | Nos
|  | ii) | 50/5 A | 2 | Nos
|  | iii) | 100/5 A | 8 | Nos
|  |  | Total | 11 |  | 41504.96 | 3448.85 |  | 5662.98 | 862.77 | 51479.56 |  | 566275.16 | 51479.56
|  |  | Total | 11 |  | 41504.96 | [6 empty] | 566275.16 | 51479.56 | 51480 | 55058
2 | M/s Heptecare Power Industries | HPSEBL/SED/SSD-289(Heptacare) | 33 kV Single Phase Outdoor Type, Live tank design, Oil Immersed, Self Cooled, CT along with Bimetatic Terminal Connector and other accessories.
I | Pvt. Ltd.A-9/10 Udyog Puram, | 2010-777-808 Dt. 23.05.2011 | CTs
| Partappur, Meerut-2501303 |  | 200-100/0.577-1-1-1 A | 6 | Nos | 25000 | 2575 |  | 551.5 | 1000 | 174759 |  | 174759 | 29126.5
|  |  | 300-150/0.577-1-1-1 A | 9 | Nos | 25500 | 2626.5 |  | 562.53 | 1000 | 267201.27 |  | 267201.27 | 29689.03
|  |  | 400-200/0.577-1-1-1 A | 9 | Nos | 24000 | 2472 |  | 529.44 | 1000 | 252012.96 |  | 252012.96 | 28001.44
|  |  | Total | 24 |  | 74500 | [6 empty] | 693973.23 | 28915.5513 | 28916 | 30926
33 kV Electromagnetic Single Phase Outdoor Type, Live tank design, Oil Immersed, Self Cooled, Hermatically Sealed VT along with Bimetatic Terminal Connector and other accessories.
PT
|  |  | 36/ 3KV /110/ 3-110/ 3- 110 V | 15 | Nos | 21392 | 2203.376 |  | 471.9075 | 1000 | 376009.2528 |  | 376009.2528 | 25067.2835
|  |  | Total | 15 |  | 21392 | [6 empty] | 376009.2528 | 25067.2835 | 25067 | 26809
| Average Rate of CTs and PTs | 11 kVCT-PT Combined Unit | Total | 60 | [8 empty] | 1451205.6 | 24186.76 | 24187 | 25868
| as per supply order No. 1 & 2 | 22kVCT-PT Combined Unit | Total | 1 | [8 empty] | 37663.75 | 37663.75 | 37664 | 40282
|  | 33kV CT-PT Combined Unit | Total | 11 | [8 empty] | 566275.16 | 51479.56 | 51480 | 55058
|  | 33 kV CTs Single Unit of Ratio | Total | 24 | [8 empty] | 693973.23 | 28915.5513 | 28916 | 30926
|  | 33 kV PTs Single Unit of Ratio | Total | 15 | [8 empty] | 376009.2528 | 25067.2835 | 25067 | 26809
P-91
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
B | 36KV VACUUM CIRCUIT BREAKERS
3 | M/S Crompton Greaves Ltd: | HPSEBL/SED/SSD-275/2010- | 1. 36KV, 1250A,25KA breaking capacity VCB suitable for 3Ph auto reclosing complete with Gang operating
I | Vandhana Building, 11 Tolstoy | CGL/2010-4238-70 Dt. 30.11.10 | machenism Auxilary Switches interlock Control Cabinet Multicore Cable terminal connectors & Accessories etc.
Marg, New Delhi-011-23324360
|  |  |  | 14 | No. | 175000 | 18025 |  | 3860.5 | 8200 | 2871197 |  | 2871197 | 205085.5
Fabricated Hot Dip galvanised steel supporting structure including foundation bolts including CT Mounting structure
|  |  |  | 14 | No. | 9500 | 978.5 |  | 209.57 | 1000 | 163632.98 |  | 163632.98 | 11688.07
2. Mandatory spares for normal operation:
|  |  | i. Tripping Coils | 9 | No. | 1000 | 103 |  | 22.06 | 50 | 10575.54 |  | 10575.54 | 1175.06
|  |  | ii. Closing Coils | 9 | No. | 1000 | 103 |  | 22.06 | 50 | 10575.54 |  | 10575.54 | 1175.06
|  |  | iii. Auxilary switch | 1 | No. | 1500 | 154.5 |  | 33.09 | 50 | 1737.59 |  | 1737.59 | 1737.59
iv. Vacuum interuptor a/w chamber and supporting insulator
|  |  |  | 4 | No. | 58000 | 5974 |  | 1279.48 | 1200 | 265813.92 |  | 265813.92 | 66453.48
|  |  | Total | 14 | [8 empty] | 3323532.57 | 237395.1836 | 237395 | 253894
| 36KV VACUUM | 36 kV 1250A, | Total | 14 | [8 empty] | 3323532.57 | 237395.1836 | 237395 | 253894
| CIRCUIT BREAKERS | 25 KA Breaking Capacity
C | ISOLATORS
4 | M/S Faraday Electricals Pvt. | HPSEBL/SE(D)ES/SSD-269 | 1. 36KV, 800A, double break, isolators triple pole, group operated, manually operated outdoor type,without Earthing switch,
I | Ltd. H-1016 road No.-14 | FEPL/10-2600-2638 | conforming to IS:9921 without solid core insulators and support structures.
| V.K.I.A, Jaipur-302013 | Dt. 19.08.10. |  | 50 | Set | 26400 | 2131.8528 |  | 560.0771 | 1000 | 30091.9299 | 528 | 1478196.4928 | 29563.9299
2. 36KV, 800A, double break, isolators triple pole, group operated, manually operated outdoor type,with Earthing switch,
conforming to IS:9921 without solid core insulators and support structures.
|  |  |  | 17 | Set | 31900 | 2575.9888 |  | 676.7598 | 1000 | 36152.7486 | 638 | 603750.7258 | 35514.7486
3. Stack of 36KV solid core insulators for above creepage 1116 mm (9 no.Per set)
|  |  |  | 67 | Set | 17050 |  |  |  | 600 | 17650 | 341 | 1159703 | 17309
III |  |  | 4. Support structure for above
|  |  |  | 2 | Nos. | 11550 | 932.6856 |  | 245.0337 | 1000 | 13727.7193 | 231 | 26993.4386 | 13496.7193
|  |  | Sub Total | [9 empty] | 3268643.6572
5. Mandatory spares for 36KV isolators
a) Isolator Blades for main contacts
|  |  |  | 2 | Nos. | 600 | 48.4512 |  | 12.729 |  | 661.1802 | 12 | 1298.3604 | 649.1802
b) Female contacts Assy. for above
|  |  |  | 2 | Nos. | 1250 | 100.94 |  | 26.5188 |  | 1377.4588 | 25 | 2704.9176 | 1352.4588
c) Bearings for central rotating post(Top& Bottem) per pole
|  |  |  | 2 | Nos. | 900 | 72.6768 |  | 19.0935 |  | 991.7703 | 18 | 1947.5407 | 973.7703
d) Pair of 6 NO : 6NC Aux. contacts
|  |  |  | 2 | Nos. | 750 | 60.564 |  | 15.9113 |  | 826.4753 | 15 | 1622.9506 | 811.4753
e) Isolator blades for Earthing switch
|  |  |  | 2 | Nos. | 750 | 60.564 |  | 15.9113 |  | 826.4753 | 15 | 1622.9506 | 811.4753
f) 36KV solid core insulators
|  |  |  | 8 | Nos. | 1770 |  |  |  |  | 1770 | 35.4 | 13876.8 | 1734.6
|  |  | Sub Total | [9 empty] | 23073.5198 | 6332.9599
|  | Isolators without Earth blade | Total | 50 | [8 empty] | 1478196.4928 | 29563.9299 | 29564 | 31619
|  | Isolators with Earth blade | Total | 17 | [8 empty] | 603750.7258 | 35514.7486 | 35515 | 37983
|  | Stack of 36KV solid core insulator | Total | 67 | [8 empty] | 1159703 | 17309 | 17309 | 18512
|  | Support structure for above | Total | 2 | [8 empty] | 26993.4386 | 13496.7193 | 13497 | 14435
|  | Spares | Total | [9 empty] | 23073.5198 | 6332.9599 | 6333 | 6773
|  | Isolators without Earth blade with Stack of 36KV solid core insulators Support structure and Spares | [11 empty] | 66702.6091 | 66703 | 71339
|  | Isolators with Earth blade with Stack of 36KV solid core insulators Support structure and Spares | [11 empty] | 72653.4278 | 72653 | 77702
P-92
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
D | 33/11KV & 33/22 kV Power TRANSFORMER:
5 | M/s Fatehpuria Transformers & | No. HPSEB/DDSS/SSD- | 6.3 MVA, 33/11 kV, ONAN Cooled , Oil imersed, Copper wound, Outdoor type,with winding connection Delta-Star, having vector group DY11, complete with fittings and acessaries
I | Switchgears (Pvt.) Ltd ,13, | 284/10-FTS/11-7317-45 |  | 12 | Nos | 2945000
| Jaipura Mansion, Tholia Circle | dated 31.03.11 | SPARES:
| MI Road, Jaipur-302001 |  | a) 36KV HV bushing complete with metal parts
|  |  |  | 2 | Nos | 2500
b) 12KV LV bushing complete with metal parts
|  |  |  | 2 | Nos | 1250
c) Complete set of baskets
|  |  |  | 2 | Sets | 5000
d) Spare winding Limb for HV & LV
|  |  |  | 1 | Sets | 500000
|  |  | e) Buchholz Relay | 1 | Nos | 5000
|  |  | Total |  |  | 35862500 | 3693837.5 |  | 791126.75 | 360000 | 40707464.25 |  | 40983214.25
|  |  | Type Test and special test: | [9 empty] | (Including Test Charges)
a) Heat Run Test
|  |  | b) Lightening Impulse voltage withstand Test |  |  | 250000 |  |  | 25750 | (Service tax on Test Charges)
|  |  | Total (Test Charges) |  |  | 275750 | (i/c Service tax)
II |  |  | 3.15 MVA, 33/11kV, ONAN Cooled , Oil imersed, Copper wound, Outdoor type,with winding connection Delta-Star, having vector group DY11, complete with fittings and acessaries
|  |  |  | 6 | Nos | 1980000
SPARES:
a) 36KV HV bushing complete with metal parts
|  |  |  | 1 | Nos | 2500
b) 12KV LV bushing complete with metal parts
|  |  |  | 1 | Nos | 1250
c) Complete set of baskets
|  |  |  | 1 | Sets | 5000
d) Spare winding Limb for HV & LV
|  |  |  | 1 | Sets | 250000
e) Buchholz Relay
|  |  |  | 1 | Nos | 5000
Any other spares
|  |  | Total |  |  | 12143750 | 1250806.25 |  | 267891.125 | 150000 | 13812447.375 |  | 14093347.375
|  |  | Type Test and special test: | [9 empty] | (Including Test Charges)
a) Heat Run Test
|  |  | b) Lightening Impulse voltage withstand Test |  |  | 250000 |  |  | 30900 | (Service tax on Test Charges)
|  |  | Total (Test Charges) |  |  | 280900
6 | M/s Fatehpur Transformers & | No. HPSEB/DDSS/SSD- | 6.3 MVA, 33/11 kV, ONAN Cooled , Oil imersed, Copper wound, Outdoor type,with winding connection Delta-Star, having vector group DY11, complete with fittings and acessaries
I | Switchgears Ltd ,13, | 284/10-FTS (Addl.)/11-4278-96 |  | 2 | Nos | 2945000
| Jaipura Mansion, Tholia Circle | dated 13.12.11 | SPARES:
| MI Road, Jaipur-302001 |  | a) 36KV HV bushing complete with metal parts
|  |  |  | 1 | Nos | 2500
b) 12KV LV bushing complete with metal parts
|  |  |  | 1 | Nos | 1250
c) Complete set of baskets
|  |  |  | 1 | Sets | 5000
|  |  | Total |  |  | 5898750 | 607571.25 |  | 130126.425 | 60000 | 6696447.675 |  | 6696447.675
|  |  | Type Test and special test: | [9 empty] | (Including Test Charges)
a) Heat Run Test
|  |  | b) Lightening Impulse voltage withstand Test |  |  | 0 |  |  | 0 | (Service tax on Test Charges)
|  |  | Total (Test Charges) |  |  | 0 | (i/c Service tax)
3.15 MVA, 33/11kV, ONAN Cooled , Oil imersed, Copper wound, Outdoor type,with winding connection Delta-Star, having vector group DY11, complete with fittings and acessaries
|  |  |  | 4 | Nos | 1980000
P-93
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
SPARES:
a) 36KV HV bushing complete with metal parts
|  |  |  | 1 | Nos | 2500
b) 12KV LV bushing complete with metal parts
|  |  |  | 1 | Nos | 1250
c) Complete set of baskets
|  |  |  | 1 | Sets | 5000
|  |  | Total |  |  | 7928750 | 816661.25 |  | 174908.225 | 100000 | 9020319.475 |  | 9020319.475
|  |  | Type Test and special test: | [9 empty] | (Including Test Charges)
a) Heat Run Test
|  |  | b) Lightening Impulse voltage withstand Test |  |  | 0 |  |  | 30900 | (Service tax on Test Charges)
|  |  | Total (Test Charges) |  |  | 0
| Average Rate of 33/11 kV | 3.15 MVA 33/11 kV | Total | 10 |  | 23113666.85 | [6 empty] | 23113666.85 | 2311366.685 | 2311367 | 2472007
|  | 6.3 MVA, 33/11 kV | Total | 14 |  | 47679661.925 | [6 empty] | 47679661.925 | 3405690.1375 | 3405690 | 3642385
E | Lightening Arrestors
7 | M/s Reychem RPG Ltd. | No. HPSEB/SEES/SSD- | 30 kV Surge Arrestor | 30 kV, Single Phase, Voltage Coordinated, Station Class, Zinc Oxide, Gapless, outdoor type, without insulating base and Discharge counters
I | 1107-1112, 11th Floor, | 287/10-Raychem/11-1515-43
| Vishwa Deep Building, Distt. Centre | dated 23.06.2011 |  | 21 | No. | 4009.5 | 0 |  | 551.3063 | 450 | 105226.9312 |  | 105226.9312
Jankapuri, New Delhi 110058
|  |  | Total | 21 |  | 4009.5 | [6 empty] | 105226.9312 | 5010.8062 | 5011 | 5359
|  |  | 18 kV Surge Arrestor | 18 kV, Single Phase, Voltage Coordinated, Station Class, Zinc Oxide, Gapless, outdoor type, without insulating base and Discharge counters
|  |  |  | 27 | No. | 3069 | 0 |  | 421.9875 | 340 | 103436.6625 |  | 103436.6625
|  |  | Total | 27 |  | 3069 | [6 empty] | 103436.6625 | 3830.9875 | 3831 | 4097
| Average Rate | 30 KV LA for 33 kV | Total | 21 |  | 4009.5 | [6 empty] | 105226.9312 | 5010.8062 | 5011 | 5359
|  | 18 KV LA for 22 kV | Total | 27 |  | 3069 | [6 empty] | 103436.6625 | 3830.9875 | 3831 | 4097
F | 33KV CONTROL & RELAY PANEL:
8 | M/s EASUN Rayrolle Limited | HPSEBL/SED-291/10(ER)/11-1023-54 | 33KV Simplex Type Transformer C&R Pannels without Differencial & with Ref Relay & with inbult LBB relay
| 98, SIPCOT Industrial Complex, | Dated 01.06.2011. |  | 5 | No. | 183000 | 18849 |  | 4036.98 | 5200 | 1055429.9 |  | 1055429.9 | 211085.98
Hosur-635126 Chennai (TN)
|  |  | Total | 5 |  | 183000 | [6 empty] | 1055429.9 | 211085.98 | 211086 | 225756
33KV Simplex Type Transformer C&R Pannels with seprate Differencial & with Ref Relay & with inbult LBB relay
|  |  |  | 2 | No. | 355000 | 36565 |  | 7831.3 | 5350 | 809492.6 |  | 809492.6 | 404746.3
|  |  | Total | 2 |  | 355000 | [6 empty] | 809492.6 | 404746.3 | 404746 | 432876
33KV SimplexType Bus Cuupler Pannels with inbult LBB relay
|  |  |  | 2 | No. | 168000 | 17304 |  | 3706.08 | 5150 | 388320.16 |  | 388320.16 | 194160.08
|  |  | Total | 2 |  | 168000 | [6 empty] | 388320.16 | 194160.08 | 194160 | 207654
33KV SimplexType Feeder Pannels with inbult LBB relay
|  |  |  | 7 | No. | 218000 | 22454 |  | 4809.08 | 5200 | 1753241.56 |  | 1753241.56 | 250463.08
|  |  | Total | 7 |  | 218000 | [6 empty] | 1753241.56 | 250463.08 | 250463 | 267870
22 KV SimplexType Feeder Pannels with inbult LBB relay
|  |  |  | 7 | No. | 218000 | 22454 |  | 4809.08 | 5200 | 1753241.56 |  | 1753241.56 | 250463.08
|  |  | Total | 7 |  | 218000 | [6 empty] | 1753241.56 | 250463.08 | 250463 | 267870
P-94
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
| Average Rate of Control and | 33 kV T/F Pannel without Diff. Relay | Total | 5 |  | 183000 | [6 empty] | 1055429.9 | 211085.98 | 211086 | 225756
| Relay Panels | 33 kV T/F Pannel with Diff. Relay | Total | 2 |  | 355000 | [6 empty] | 809492.6 | 404746.3 | 404746 | 432876
|  | 33 kV Bus Coupler Pannel |  | 2 |  | 168000 | [6 empty] | 388320.16 | 194160.08 | 194160 | 207654
|  | 33 kV Feeder Pannel |  | 7 |  | 218000 | [6 empty] | 1753241.56 | 250463.08 | 250463 | 267870
|  | 22 kV Feeder Pannel |  | 7 |  | 218000 | [6 empty] | 1753241.56 | 250463.08 | 250463 | 267870
G | 12KV INDOOR SWITCHGEAR PANEL BOARDS.
9 | M/s Megawin Switchgears Pvt. | DDSS/SSD-267/(MEGAWIN)
I | Ltd, Post Box No. 434 | 08-2229-39 | 12 kV 800 A ,12.5 KA
| Alagapuram Post | Dt. 12.08.09 | i) 10 Panel Board | 1 | set | 2129100 | 307016.22 |  | 304514.5275 | 100000 | 2840630.7475 |  | 2840630.7475
| Perumal, Malaiadivaram |  | ii) 9 Panel Board | 1 | set | 1926000 | 277729.2 |  | 275466.15 | 90000 | 2569195.35 |  | 2569195.35
| Selem(TN)-636004 |  | iii) 9 Panel Board | 1 | set | 1926000 | 277729.2 |  | 275466.15 | 90000 | 2569195.35 |  | 2569195.35
|  |  | iv) 2 Panel Board | 1 | set | 408200 | 58862.44 |  | 58382.805 | 20000 | 545445.245 |  | 545445.245
|  |  | v) 1 Panel Board | 1 | set | 204100 | 29431.22 |  | 29191.4025 | 10000 | 272722.6225 |  | 272722.6225
iv) Spares
|  |  | a) Tripping Coil | 3 | No. | 1800 | 259.56 |  | 257.445 | 50 | 7101.015 |  | 7101.015
|  |  | b) Closing Coil | 3 | No. | 1800 | 259.56 |  | 257.445 | 50 | 7101.015 |  | 7101.015
|  |  | c) Vacuum Interrupter | 1 | No. | 15000 | 2163 |  | 2145.375 | 194 | 19502.375 |  | 19502.375
d) C.T. of Metering AC-0.5
|  |  | I. 600-300/1-1-0.577-1A | 1 | No. | 7000 | 1009.4 |  | 1001.175 | 230 | 9240.575 |  | 9240.575
|  |  | II. 300-150/1-1-0.577-1A | 1 | No. | 7000 | 1009.4 |  | 1001.175 | 230 | 9240.575 |  | 9240.575
|  |  | III. 200-100/1-1-1A | 1 | No. | 7000 | 1009.4 |  | 1001.175 | 230 | 9240.575 |  | 9240.575
|  |  | IV. 100-50/1-1-1A | 1 | No. | 7000 | 1009.4 |  | 1001.175 | 230 | 9240.575 |  | 9240.575
|  |  | e) TVM | 1 | No. | 10000 | 1442 |  | 1430.25 | 250 | 13122.25 |  | 13122.25
|  |  | Total |  |  | 6650000 | 958930 |  | 951116.25 | 311464 | 8880978.27 |  | 8880978.27
| Average Rate of 12 kV Indoor | Panel Board | Total (31 Panel) | 31 | [8 empty] | 8797189.315 | Average Rate for one no. Panel (Rs.)=
| Switchgear Pannel Board | Spares
| As per Supply Order NO. 5 | a) Tripping Coil | Total | 3 | No. | [7 empty] | 7101.015
|  | b) Closing Coil | Total | 3 | No. | [7 empty] | 7101.015 |  |  | 333816
|  | c) Vacuum Interrupter | Total | 1 | No. | [7 empty] | 19502.375
|  | CT for Metring AC-.5 | [12 empty] | 286483 | with hike for 2012-13
|  | I. 600-300/1-1-0.577-1A | Total | 1 | No. | [7 empty] | 9240.575
|  | II. 300-150/1-1-0.577-1A |  | 1 | No. | [7 empty] | 9240.575
|  | III. 200-100/1-1-1A |  | 1 | No. | [7 empty] | 9240.575
|  | IV. 100-50/1-1-1A |  | 1 | No. | [7 empty] | 9240.575
|  | e) TVM |  | 1 | No. | [7 empty] | 13122.25

## 12 kV VCB
S. | SUPPLIER | P.O.NO. & DATE | DESCRIPTION | QTY | UNIT | RATE | E.D | Edu. | SALE | F&I,UN- |  | DIS- | GRAND | UNIT | ROUNDED | ROUNDED
NO | [7 empty] | Cess | TAX/VAT | LOADING | TOTAL | COUNT | TOTAL | RATE | RATE | RATE
[10 empty] | CHARGES |  |  |  |  | 2009-10 | 2010-11
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
A | 12 kV VACUUM CIRCUIT BREAKER
1 | M/S Afstom Ltd. | DDS/SSD-205/03 -VCB/ | 12 KV 630A ,3 Phase,outdoor type, self
| Sector 34 A | 2004 2929-48 dt. 4.9.04 | powered outdoor type vacuum
| CHANDIGARH-22 |  | circuit breaker with Auto
Reclose scheme
|  |  | Current Transformer,Potential | 23 |  | 250000 |  |  | 920000 | 179400 |  |  | 6849400 | 297800
T/former,Relays,Metering &
including instruments, Control
T/former and copper Bus
Bar etc.
Complete with all accessories ,
Heaving the following C.T.
Ratios
|  |  | 1)300-150 /5-5 A | 9 |  | 2500 |  |  | 3600 | 675 |  |  | 26775
|  |  | 2)100-50 /5-5 A | 9 |  | 800 |  |  | 1152 | 216 |  |  | 8568
|  |  | 3) 60-30 /5-5 A | 15 |  | 12000 |  |  | 28800 | 5400 |  |  | 214200
2)Trip Coils
3) Closing coils
Vacume Intrupters (V204 )
C.T. Ratios
|  |  | 1)300-150 /5-5 A | 15 |  | 7300 |  |  | 17520 | 3285 |  |  | 130305
2)100-50 /5-5 A
3)60-30 /5-5 A
| 12 KV VACUUM | 12 kV 630A, | Total | 23 | [8 empty] | 6849400 | 297800 | 297800 | 297800
| CIRCUIT BREAKERS | [10 empty] | Say Rs. with 10% Hike for 2011-12= | 327580 | Rate for 2012-13= |  | 350346.81

## Sheet1
ANALYSIS OF 12 kV VCB RATE
Sr. No. | Description | Unit | Rate as per |  | Difference (PO-CD) | % Difference w.r.t CD | Avrerage % increase/ decrease
|  |  | PO 2010-11 | Cost Data 2010-11
| 33 kV VCB | No. | 237395 | 348313 | -110918 | -31.8443 | -31.8443
Threfore the Rates of VCB taken in Cost data for which no PO have been placed during 2010-11
=Rate as Per CDx(1+%increase/Decrease/100)
|  |  | CD 2010-11 Rate | Rate
| 12 kV VCB RATE | No. | 327580 | 223264.2884