## Page-4 to 6
Page-4 to 6
Determination of normative rates per kW/kVA for the connected load/contract demand as per Regulation 5(2) of HPERC Regulation 419/2012
I) Calculation of per KW/KVA cost for load up to 50 kW (load to be released on LT)
Details of Works Taken in the calculations:-
| 1) Incoming line per DTR ( 11 kV ) |  | 0.25 | kM
| 2) Transformer (11/0.4 kV) |  | 25 kVA (1 NO.), 63 kVA (1 No.), 100 kVA (1 NO.), 250 kVA(1NO.)
|  | Total KVA | 438 | kVA
Utilisation factor for feeding 11 kV line
| Calculating capacity of 11 kV line |  | 2600.598 | kVA
| Utilisation factor( DTR Capacity/Capacity of 11 kV line) |  |  | 0.16842
| 3 Outgoing Feeders(LT) per DTR |  | 0.125 | kM
Sr. No. | Item Description | Unit | Rate per Unit(Rs) | Quantity taken | Utilisation Factors for line |  | Amount(Rs)
1 | Incoming 11 kV Line | kM | 338348.7898 | 1 | 0.16842 |  | 56985.651
2 | DTR
| 25 kVA | No | 160144.4453 | 1 |  |  | 160144.4453
| 63 kVA | No | 207602.616 | 1 |  |  | 207602.616
| 100 kVA | No | 250072.8741 | 1 |  |  | 250072.8741
| 250 kVA | No | 365217.1102 | 1 |  |  | 365217.1102
3 | Outgoing feeder(LT) | kM | 322136.4359 | 0.5 |  |  | 161068.218
|  | TOTAL COST | (A) |  |  |  | 1201090.9145
|  | Capacity Created(kVA) |  |  | 438
i) per kW cost for single part tariff consumers i.e. connected load up to 20 kW
The consumer are regulated with connected load and the demand factor of the domestic and non-residential consumers are 30% and 40 % as per Supply Code. In view of this , the per kW charges are worked out as under:-
Sr. No. | Description |  |  | Domestic supply |  | Non-residential Supply
1 | Capacity Created(kVA) |  |  | 438 |  | 438
2 | Capacity kVA taking 30% demand Factor for Domestic and 40 % for Non-residential |  |  | 1460 |  | 1095
3 | Capacity kW by taking 0.9 pf |  |  | 1314 |  | 985.5
4 | per kW rate (Total Cost/ Capacity kW) |  |  | 910 |  | 1220
| ii) per kVA for consumers above 20 kW up to 50 kW = |  |  | Rs | 2740 | [ Total Cost/ 438]
II) Calculation of per kVA cost for load between 50 kW and 2000 kW for general load and up to 1000 kW for furnace / rolling load and load to be released on 11 kV
Details of Works Taken in the calculations:-
1) | 33/11 kV, Sub-Stations
| i) Incoming line ( 33 kV ) |  |  |  |  | 12 | kM
| ii) Transformer (33/11 kV) |  |  |  |  | 3.15 | MVA
| iii) Outgoing Feeder(11 kV) |  |  |  |  | 11 | kM
iv) Utilisation factor for feeding 33 kV line
| Calculated Capacity of 33 kV line |  |  |  |  | 13.003 | MVA
| Utilisaation Factor (Sub-Station rating/capacity) |  |  |  |  | 0.24225
2) | 66/11 kV, Sub-Stations
| i) Incoming line ( 66 kV ) |  |  |  |  | 25
| ii) Transformer (66/11 kV) |  |  |  |  | 20 | MVA
| iii) Outgoing Feeder(11 kV) |  |  |  |  | 11
iv) Utilisation Factor for feeding 66 kV line
| Calculated line Capacity |  |  |  | 31.6073 | MVA
| Utilisation factor for load of sub-station taken [Sub-Station Capacity/ line capacity] |  |  |  | 0.63277
3) | 132/11 kV, Sub-Stations
| i) Incoming line ( 132 kV ) |  |  |  |  | 26 | kM
| ii) Transformer (132/11 kV) |  |  |  |  | 31.5 | MVA
iii) Utilisation Factors for feeding 132 kV line
| Calculated line Capacity |  |  |  |  | 76.0175 | MVA
| Utilisation factor for load of sub-station taken [Sub-Station Capacity/ line capacity] |  |  |  |  | 0.41438
| iv) Outgoing Feeder(11 kV) |  |  |  |  | 11 | kM
Sr. No. | Item Description | Unit | Rate per Unit(Rs) | Qty | Utilisation Factors for line | Amount(Rs) | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 (4*5*6)
1 | Incoming lines
| i) 33 kV | kM | 808324.4993 | 12 | 0.24225 | 2349818.4704
| ii) 66 kV | kM | 131653732.0849 | Total | 0.63277 | 83305986.5123
| iii) 132 kV | kM | 174695391.0232 | Total | 0.41438 | 72389992.6337
2 | Transformers
| 33/11 kV | No | 11875636.2204 | 1 |  | 11875636.2204
| 66/11 kV | No | 40366734.6317 | 1 |  | 40366734.6317
| 132/11 kV | No | 44511165.3241 | 1 |  | 44511165.3241
3 | Outgoing lines
| 11 kV | kM | 338348.7898 | 33 | NA | 11165510.0647
| TOTAL |  |  |  |  | 265964843.8573
|  |  | Capacity Created(kVA) |  |  | 54650
|  |  | Per kVA rate(Rounded to 10) |  |  | 4870
III) Calculation of per kVA cost for load between 1000 kW and 10000 kW for for furnace / rolling load and between 2000 kW & 10000 for general load to be released on 33 kV
Details of Works Taken in the calculations:-
1) | 66/33 kV
| i) Incoming line ( 66 kV ) |  |  |  |  | 25 | kM
| ii) Transformer (66/33 kV) |  |  |  |  | 20 | MVA
| iv) Outgoing Feeder(33 kV) |  |  |  |  | 12 | kM
Utilisation factor for feeding 66 kV line
| Calculated line Capacity |  |  |  | 31.6073
| Utilisation factor for load of sub-station taken [Sub-Station Capacity/ line capacity] |  |  |  | 0.63277
2) | 132/33 kV, Sub-Stations
| i) Incoming line ( 132 kV ) |  |  |  |  | 26 | kM
| ii) Transformer (132/33 kV) |  |  |  |  | 31.5 | MVA
| iv) Outgoing Feeder(33 kV) |  |  |  |  | 12 | kM
Utilisation factor for feeding 132 kV line
| Calculated line Capacity |  |  |  | 76.0175
| Utilisation factor for load of sub-station taken [Sub-Station Capacity/ line capacity] |  |  |  | 0.41438
3) | 220/33 kV, Sub-Stations
| i) Incoming line ( 220 kV ) |  |  |  |  | 27 | kM
| ii) Transformer (220/33 kV) |  |  |  |  | 31.5 | MVA
| iii) Outgoing Feeder(33 kV) |  |  |  |  | 12 | kM
iv) Utilisation factor for feeding 220 kV line
| Calculated line Capacity |  |  |  |  | 196.0451
| Utilisation factor for load of sub-station taken [Sub-Station Capacity/ line capacity] |  |  |  |  | 0.16068
Sr. No. | Item Description | Unit | Rate per Unit(Rs) | Quantity taken | Utilisation Factors for line | Amount(Rs) | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7(4*5*6)
1 | Incoming lines
| i) 66 kV | kM | 131653732.0849 | 1 | 0.63277 | 83305986.5123 | Rate for specified quantity already included in the unit rate
| ii) 132 kV | kM | 174695391.0232 | 1 | 0.41438 | 72389992.6337
| iii) 220 kV | kM | 260956748.5288 | 1 | 0.16068 | 41929833.5804
2 | Transformers
| 66/33 kV | No | 40100142.8607 | 1 |  | 40100142.8607
| 132/33 kV | No | 45163211.4393 | 1 |  | 45163211.4393
| 220/33 kV | No | 72815966.6379 | 1 |  | 72815966.6379
3 | Outgoing lines
| 33 kV | kM | 808324.4993 | 36 | NA | 29099681.9736
| TOTAL |  |  |  |  | 384804815.6379
|  | Capacity Created(kVA) |  |  |  | 83000
|  | Per kVA rate(Rounded to 10) |  |  |  | 4640
IV) Calculation of per kVA cost for load between 1000 kW and 10000 kW for for furnace / rolling load and between 2000 kW & 10000 for general load to be released on 66 kV
Details of Works Taken in the calculations:-
220/66 kV, Sub-Stations
| i) Incoming line ( 220 kV ) |  |  |  |  | 27 | kM
| ii) Transformer (220/66 kV) |  |  |  |  | 100 | MVA
| iv) Outgoing Feeder(66 kV) |  |  |  |  | 25 | kM
Utilisation factor feeding 220 kV line
| Calculated line Capacity |  |  |  | 196.0451
| Utilisation factor for load of sub-station taken [Sub-Station Capacity/ line capacity] |  |  |  | 0.51009
Sr. No. | Item Description | Unit | Rate per Unit(Rs) | Quantity taken | Utilisation Factors for line | Amount(Rs) | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7(4*5*6)
1 | Incoming lines
| 220 kV | kM | 260956748.5288 | 1 | 0.51009 | 133110582.7949 | Rate for specified quantity already included in the unit rate
2 | Transformers
| 220/66 kV | No | 161571069.9294 | 1 |  | 161571069.9294
3 | Outgoing lines
| 66 kV | kM | 131653732.0849 | 1 | NA | 131653732.0849 | Rate for specified quantity already included in the unit rate
| TOTAL |  |  |  |  | 426335384.8093
|  |  | Capacity Created(kVA) |  |  | 100000
|  |  | Per kVA rate(Rounded to 10) |  |  | 4260
V) Calculation of per kVA cost for load above 10000 kW and load to be released on 132 kV or 220 kV
Details of Works Taken in the calculations:-
| i) Incoming line ( 220 kV ) |  |  |  |  | 27 | kM
| ii) Transformer (220/132kV) |  |  |  |  | 100 | MVA
| iii) Outgoing Feeder(132 kV) |  |  |  |  | 26 | kM
Utilisation factor feeding 220 kV line
| Calculated line Capacity |  |  |  | 196.0451
| Utilisation factor for load of sub-station taken [Sub-Station Capacity/ line capacity] |  |  |  | 0.51009
Sr. No. | Item Description | Unit | Rate per Unit(Rs) | Quantity taken | Utilisation Factors for line | Amount(Rs) | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7(4*5*6)
1 | Incoming line 220 kV |  | 260956748.5288 | 1 | 0.51009 | 133110582.7949 | Rate for specified quantity already included in the unit rate
2 | Transformers
| 220/132 kV | No | 101431055.5014 | 1 | 1 | 101431055.5014
3 | Outgoing lines
| 132 kV | kM | 174695391.0232 | 26 | NA | 174695391.0232 | Rate for specified quantity already included in the unit rate
| TOTAL |  |  |  |  | 409237029.3196
|  |  | Capacity Created(kVA) |  |  | 100000
|  |  | Per kVA rate(Rounded to 10) |  |  | 4090

## Page-18- 20
Page 18-20
Calculations of cost for EHV lines based on approved cost data for the year 2011-12
Calculation of cost of 66 kV Single Circuit line
Sr. No. | Item Description | Rate (Rs Lac) | Unit | Qty | Amount (Rs Lac)
1 | Preliminary Works
| i) Temp. Sheds | 0.29 | kM | 25 | 7.25
| ii) Reconnaisance and Preliminary Survey | 0.3 | kM | 25 | 7.5
| iii) Detailed Surveying | 0.83 | kM | 25 | 20.75
2 | Compensation for land, trees, Crops, Tree Cutting and Afforestation etc. | 1.856 | kM | 25 | 46.4
3 | Cost for 66 kV line | 28.27 | kM | 25 | 706.75
4 | NPV Charges(=40% of length of line xW/10000) | 9.39 | Hect. | 18 | 169.02
5 | Cost of terminal Eqpt. At both ends(P-87) | 57.14 | No | 2 | 114.28
6 | PLCC Equipments | 32.82 | No | 2 | 65.64
| Sub-Total |  |  |  | 1137.59
7 | Add. 3 % Contingency |  |  |  | 34.1277
| Sub-Total |  |  |  | 1171.7177
8 | Add. 11 % Departmental Charges |  |  |  | 128.8889
| Sub-Total |  |  |  | 1300.6066
9 | Add. 12.36 % Service Tax on DC |  |  |  | 15.9307
| GRAND TOTAL |  |  |  | 1316.5373
Calculation of cost of 132 kV Single Circuit Line |  |  |  |  | Page-19
Sr. No. | Item Description | Rate (Rs Lac) | Unit | Qty | Amount (Rs Lac)
1 | Preliminary Works
| i) Temp. Sheds | 0.29 | kM | 26 | 7.54
| ii) Reconnaisance and Preliminary Survey | 0.3 | kM | 26 | 7.8
| iii) Detailed Surveying | 0.83 | kM | 26 | 21.58
2 | Compensation for land, trees, Crops, Tree Cutting and Afforestation etc. | 2.032 | kM | 26 | 52.832
3 | Cost for 132 kV line | 34.96 | kM | 26 | 908.96
4 | NPV Charges(=40% length of line xW/10000) | 9.39 | Hect. | 28.08 | 263.6712
5 | Cost of terminal Eqpt. At both ends[single bus bar] | 85.86 | No | 2 | 171.72
6 | PLCC Equipments | 37.7 | No | 2 | 75.4
| Sub-Total |  |  |  | 1509.5032
7 | Add. 3 % Contingency |  |  |  | 45.2851
| Sub-Total |  |  |  | 1554.7883
8 | Add. 11 % Departmental Charges |  |  |  | 171.0267
| Sub-Total |  |  |  | 1725.815
9 | Add. 12.36 % Service Tax on DC |  |  |  | 21.1389
| GRAND TOTAL |  |  |  | 1746.9539
Calculation of cost of 220 kV Single Circuit Line |  |  |  |  | Page-20
Sr. No. | Item Description | Rate (Rs Lac) | Unit | Qty | Amount (Rs Lac)
1 | Preliminary Works
| i) Temp. Sheds | 0.29 | kM | 27 | 7.83
| ii) Reconnaisance and Preliminary Survey | 0.3 | kM | 27 | 8.1
| iii) Detailed Surveying | 0.83 | kM | 27 | 22.41
2 | Compensation for land, trees, Crops, Tree Cutting and Afforestation etc. | 2.498 | kM | 27 | 67.446
3 | Cost for 220 kV line | 50.22 | kM | 27 | 1355.94
4 | NPV Charges(=40 % of length of line xW/10000) | 9.39 | Hect. | 37.8 | 354.942
5 | Cost of terminal Eqpt. At both ends | 176.7 | No | 2 | 353.4
6 | PLCC Equipments | 42.4 | No | 2 | 84.8
| Sub-Total |  |  |  | 2254.868
7 | Add. 3 % Contingency |  |  |  | 67.646
| Sub-Total |  |  |  | 2322.514
8 | Add. 11 % Departmental Charges |  |  |  | 255.4765
| Sub-Total |  |  |  | 2577.9906
9 | Add. 12.36 % Service Tax on DC |  |  |  | 31.5769
| GRAND TOTAL |  |  |  | 2609.5675
Note : Single Circuit line has been taken keeping in view that the cost of one transformer is to be taken while working out the normative rates.

## Page 11 to 17
Page 11 to 17
Calculations of cost for EHV Sub-Stations based on approved cost data for the year 2011-12
Calculation of Cost of 66/33 kV, 1x 20 MVA Sub-Station
Sr. No. | Item Description | Rate (Rs Lac) | Unit | Qty | Amount (Rs Lac) | Quantity/Amount to be taken for normative rates as per Regulations 5(2)(i) |  | Remarks
[6 empty] | Qty. | Amount (Rs.Lac)
1 | 66/33 kV, 1x16MVA Transformer | 171.21 | No | 1 | 171.21 | 1 | 171.21
2 | 66 kV Equipment Transformer Bay
| Circuit Breaker | 6.18 | No | 1 | 6.18 | 1 | 6.18
| Control & Relay Panels | 4.46 | No | 1 | 4.46 | 1 | 4.46
| Isolators without Earth blade | 2.12 | No | 2 | 4.24 | 2 | 4.24
| Multicore Multi ratio CTs | 0.72 | No | 3 | 2.16 | 3 | 2.16
| Lighting Arrestors | 0.19 | No | 3 | 0.57 | 3 | 0.57
| PTs | 0.8 | No | 3 | 2.4 | 3 | 2.4
3 | 33 kV Equipments
| Circuit Breaker | 3.11 | No | 1 | 3.11 | 1 | 3.11
| Contral & Relay Panels | 5.2 | No | 1 | 5.2 | 1 | 5.2
| Isolators without Earth blade | 0.55 | No | 2 | 1.1 | 2 | 1.1
| Multicore Multi ratio CTs | 0.28 | No | 3 | 0.84 | 3 | 0.84
| Lighting Arrestors | 0.05 | No | 3 | 0.15 | 3 | 0.15
| PTs | 0.18 | No | 3 | 0.54 | 3 | 0.54
4 | General Equipments
| DC Battery ( 200 AH) | 3.82 | No | 1 | 3.82 | 0 | 0
| Battery Charger | 1.93 | No | 2 | 3.86 | 0 | 0
| DCDB | 0.65 | No | 1 | 0.65 | 0 | 0
| Station T/F | 4.56 | No | 1 | 4.56 | 0 | 0
| ACDB | 4.91 | No | 1 | 4.91 | 0 | 0
5 | SCADA
| RTU | 23.33 | No | 1 | 23.33 | 0 | 0
| LDMS | 10.54 | No | 1 | 10.54 | 0 | 0
| FOTE | 18.23 | No | 2 | 36.46 | 0 | 0
[5 empty] | 290.29 |  | 202.16
6 | Sub-Station Structures | 10.26 | LS | 1 | 10.26 | 0 | 0
| Sub-Total-A |  |  |  | 300.55 |  | 202.16
7 | Equipment Structure including Bus Bar, earthing, hardware fitting etc. @ 10 % |  |  |  | 30.055 |  | 20.216 | Part of Transformer and Bay, therefore included
8 | Power & Control Cables , earthmat etc. @ 13 % |  |  |  | 39.0715 |  | 13.1404 | Power and Control Cables portion charged @ 6.5%
9 | Spares @ 3% of 1 to 5 above |  |  |  | 8.7087 |  | 6.0648
10 | CST 4%, Transportation @5% , Insurance @1% Total 10 %( on 1 to 6) |  |  |  | 30.055 |  | 20.216
| Sub-Total |  |  |  | 408.4402 |  | 261.7972
11 | Storage @ 3% |  |  |  | 12.2532 |  | 7.8539
| Sub-Total |  |  |  | 420.6934 |  | 269.6511
12 | Erection Charges @ 10 % |  |  |  | 42.0693 |  | 26.9651
| Sub-Total |  |  |  | 462.7627 |  | 296.6162
13 | Civil Works
| i) 66 kV Bay | 31.31 | No | 1 | 31.31 | 1 | 31.31
| ii) 33 kV bay | 18.57 | No | 1 | 18.57 | 1 | 18.57
| iii) Sub-Station Building | 42.12 | No | 1 | 42.12 | 0 | 0
| iv) Workshop Building | 8.43 | No | 1 | 8.43 | 0 | 0
| v) Workshop Machinery | 2.83 | No | 1 | 2.83 | 0 | 0
| Sub-Total |  |  |  | 566.0227 |  | 346.4962
14 | Contingency @ 3% |  |  |  | 16.9807 |  | 10.3949
| Sub-Total |  |  |  | 583.0034 |  | 356.8911
15 | Departmental charges @11 % |  |  |  | 64.1304 |  | 39.258
| Sub-Total |  |  |  | 647.1338 |  | 396.1491
16 | Add. 12.36 % Service Tax on DC |  |  |  | 7.9265 |  | 4.8523
| GRAND TOTAL |  |  |  | 655.0603 |  | 401.0014
Calculation of Cost of 66/11 kV, 1x 20 MVA Sub-Station | [6 empty] | Page-12
Sr. No. | Item Description | Rate (Rs Lac) | Unit | Qty | Amount (Rs Lac) | Quantity/Amount to be taken for normative rates as per Regulations 5(2)(i) |  | Remarks
[6 empty] | Qty. | Amount (Rs.Lac)
1 | 66/33 kV, 1x 20 MVA Transformer | 171.21 | No | 1 | 171.21 | 1 | 171.21
2 | 66 kV Equipment Transformer Bay | [5 empty] | 0
| Circuit Breaker | 6.18 | No | 1 | 6.18 | 1 | 6.18
| Control & Relay Panels | 4.46 | No | 1 | 4.46 | 1 | 4.46
| Isolators without Earth blade | 2.12 | No | 2 | 4.24 | 2 | 4.24
| Multicore Multi ratio CTs | 0.72 | No | 3 | 2.16 | 3 | 2.16
| Lighting Arrestors | 0.19 | No | 3 | 0.57 | 3 | 0.57
| PTs | 0.8 | No | 3 | 2.4 | 3 | 2.4
3 | 11 kV Switchgear and allied equipments comprising of Panel Board, CTs, PTs etc. | 12.51 | No | 1 | 12.51 | 1 | 12.51
4 | General Equipments | [5 empty] | 0
| DC Battery ( 200 AH) | 3.82 | No | 1 | 3.82 | 0 | 0
| Battery Charger | 1.93 | No | 2 | 3.86 | 0 | 0
| DCDB | 0.65 | No | 1 | 0.65 | 0 | 0
| Station T/F | 3.42 | No | 1 | 3.42 | 0 | 0
| ACDB | 4.91 | No | 1 | 4.91 | 0 | 0
5 | SCADA | [5 empty] | 0
| RTU | 23.33 | No | 1 | 23.33 | 0 | 0
| LDMS | 10.54 | No | 1 | 10.54 | 0 | 0
| FOTE | 18.23 | No | 2 | 36.46 | 0 | 0
[5 empty] | 290.72 |  | 203.73
6 | Sub-Station Structures | 10.26 | LS | 1 | 10.26 | 0 | 0
| Sub-Total-A |  |  |  | 300.98 |  | 203.73
7 | Equipment Structure including Bus Bar, earthing, hardware fitting etc. @ 10 % |  |  |  | 30.098 |  | 20.373 | Part of Transformer and Bay, therefore included
8 | Power & Control Cables , earthmat etc. @ 13 % |  |  |  | 39.1274 |  | 13.2425 | Power and Control Cables portion charged @ 6.5%
9 | Spares @ 3% of 1 to 5 above |  |  |  | 8.7216 |  | 6.1119
10 | CST 4%, Transportation @5% , Insurance @1% Total 10 %( on 1 to 6) |  |  |  | 30.098 |  | 20.373
| Sub-Total |  |  |  | 409.025 |  | 263.8304
11 | Storage @ 3% |  |  |  | 12.2708 |  | 7.9149
| Sub-Total |  |  |  | 421.2958 |  | 271.7453
12 | Erection Charges @ 10 % |  |  |  | 42.1296 |  | 27.1745
| Sub-Total |  |  |  | 463.4253 |  | 298.9198
13 | Civil Works
| i) 66 kV Bay | 31.31 | No | 1 | 31.31 | 1 | 31.31
| ii) 33 kV bay | 18.57 | No | 1 | 18.57 | 1 | 18.57
| iii) Sub-Station Building | 42.12 | No | 1 | 42.12 | 0 | 0
| iv) Workshop Building | 8.43 | No | 1 | 8.43 | 0 | 0
| v) Workshop Machinery | 2.83 | No | 1 | 2.83 | 0 | 0
| Sub-Total |  |  |  | 566.6853 |  | 348.7998
14 | Contingency @ 3% |  |  |  | 17.0006 |  | 10.464
| Sub-Total |  |  |  | 583.6859 |  | 359.2638
15 | Departmental charges @11 % |  |  |  | 64.2054 |  | 39.519
| Sub-Total |  |  |  | 647.8913 |  | 398.7828
16 | Add. 12.36 % Service Tax on DC |  |  |  | 7.9358 |  | 4.8846
| GRAND TOTAL |  |  |  | 655.8271 |  | 403.6673
Calculation of Cost of 132/33 kV, 25/31.5 MVA Sub-Station | [6 empty] | Page-13
Sr. No. | Item Description | Rate (Rs Lac) | Unit | Qty | Amount (Rs Lac) | Quantity/Amount to be taken for normative rates as per Regulations 5(2)(i) |  | Remarks
[6 empty] | Qty. | Amount (Rs.Lac)
1 | 132/33 kV, 1x 25 MVA Transformer | 227.2 | No | 1 | 227.2 | 1 | 227.2
2 | 132 kV Equipment Transformer Bay
| Circuit Breaker | 7.89 | No | 1 | 7.89 | 1 | 7.89
| Control & Relay Panels | 4.46 | No | 1 | 4.46 | 1 | 4.46
| Isolators without Earth blade | 3.58 | No | 2 | 7.16 | 2 | 7.16
| Multicore Multi ratio CTs | 0.99 | No | 3 | 2.97 | 3 | 2.97
| Lighting Arrestors | 0.34 | No | 3 | 1.02 | 3 | 1.02
| PTs | 0.99 | No | 3 | 2.97 | 3 | 2.97
3 | 33 kV Equipments
| Circuit Breaker | 3.11 | No | 1 | 3.11 | 1 | 3.11
| Control & Relay Panels | 5.2 | No | 1 | 5.2 | 1 | 5.2
| Isolators without Earth blade | 0.55 | No | 2 | 1.1 | 2 | 1.1
| Multicore Multi ratio CTs | 0.28 | No | 3 | 0.84 | 3 | 0.84
| Lighting Arrestors | 0.05 | No | 3 | 0.15 | 3 | 0.15
| PTs | 0.18 | No | 3 | 0.54 | 3 | 0.54
4 | General Equipments
| DC Battery ( 200 AH) | 3.82 | No | 1 | 3.82 | 0 | 0
| Battery Charger | 1.93 | No | 2 | 3.86 | 0 | 0
| DCDB | 0.65 | No | 1 | 0.65 | 0 | 0
| Station T/F | 4.56 | No | 1 | 4.56 | 0 | 0
| ACDB | 4.91 | No | 1 | 4.91 | 0 | 0
5 | SCADA
| RTU | 23.33 | No | 1 | 23.33 | 0 | 0
| LDMS | 10.54 | No | 1 | 10.54 | 0 | 0
| FOTE | 18.23 | No | 2 | 36.46 | 0 | 0
[5 empty] | 352.74 |  | 264.61
6 | Sub-Station Structures | 15.39 | LS | 1 | 15.39 | 0 | 0
| Sub-Total-A |  |  |  | 368.13 | 0 | 264.61
7 | Equipment Structure including Bus Bar, earthing, hardware fitting etc. @ 10 % |  |  |  | 36.813 |  | 26.461 | Part of Transformer and Bay, therefore included
8 | Power & Control Cables , earthmat etc. @ 13 % |  |  |  | 47.8569 |  | 17.1996 | Power and Control Cables portion charged @ 6.5%
9 | Spares @ 3% of 1 to 5 above |  |  |  | 10.5822 |  | 7.9383
10 | CST 4%, Transportation @5% , Insurance @1% Total 10 %( on 1 to 6) |  |  |  | 36.813 |  | 26.461
| Sub-Total |  |  |  | 500.1951 |  | 342.6699
11 | Storage @ 3% |  |  |  | 15.0059 |  | 10.2801
| Sub-Total |  |  |  | 515.201 |  | 352.95
12 | Erection Charges @ 10 % |  |  |  | 51.5201 |  | 35.295
| Sub-Total |  |  |  | 566.721 |  | 388.2451
13 | Civil Works
| i) 132 kV Bay | 39.16 | No | 1 | 39.16 | 1 | 1
| ii) 33 kV bay | 18.57 | No | 1 | 18.57 | 1 | 1
| iii) Sub-Station Building | 56.17 | No | 1 | 56.17 | 0 | 0
| iv) Workshop Building | 8.43 | No | 1 | 8.43 | 0 | 0
| v) Workshop Machinery | 2.83 | No | 1 | 2.83 | 0 | 0
| Sub-Total |  |  |  | 691.881 |  | 390.2451
14 | Contingency @ 3% |  |  |  | 20.7564 |  | 11.7074
| Sub-Total |  |  |  | 712.6375 |  | 401.9524
15 | Departmental charges @11 % |  |  |  | 78.3901 |  | 44.2148
| Sub-Total |  |  |  | 791.0276 |  | 446.1672
16 | Add. 12.36 % Service Tax on DC |  |  |  | 9.689 |  | 5.4649
| GRAND TOTAL |  |  |  | 800.7166 |  | 451.6321
Calculation of Cost of 132/11 kV, 25/31.5 MVA Sub-Station | [6 empty] | Page-14
Sr. No. | Item Description | Rate (Rs Lac) | Unit | Qty | Amount (Rs Lac) | Quantity/Amount to be taken for normative rates as per Regulations 5(2)(i) |  | Remarks
[6 empty] | Qty. | Amount (Rs.Lac)
1 | 132/33 kV, 1x 25 MVA Transformer | 221.79 | No | 1 | 221.79 | 1 | 221.79
2 | 132 kV Equipment Transformer Bay
| Circuit Breaker | 7.89 | No | 1 | 7.89 | 1 | 7.89
| Control & Relay Panels | 4.46 | No | 1 | 4.46 | 1 | 4.46
| Isolators without Earth blade | 3.58 | No | 2 | 7.16 | 2 | 7.16
| Multicore Multi ratio CTs | 0.99 | No | 3 | 2.97 | 3 | 2.97
| Lighting Arrestors | 0.34 | No | 3 | 1.02 | 3 | 1.02
| PTs | 0.99 | No | 3 | 2.97 | 3 | 2.97
3 | 11 kV Switchgear and allied equipments comprising of Panel Board, CTs, PTs etc. | 12.51 | No | 1 | 12.51 | 1 | 12.51
4 | General Equipments
| DC Battery ( 200 AH) | 3.82 | No | 1 | 3.82 | 0 | 0
| Battery Charger | 1.93 | No | 2 | 3.86 | 0 | 0
| DCDB | 0.65 | No | 1 | 0.65 | 0 | 0
| Station T/F | 3.42 | No | 1 | 3.42 | 0 | 0
| ACDB | 4.91 | No | 1 | 4.91 | 0 | 0
5 | SCADA
| RTU | 23.33 | No | 1 | 23.33 | 0 | 0
| LDMS | 10.54 | No | 1 | 10.54 | 0 | 0
| FOTE | 18.23 | No | 2 | 36.46 | 0 | 0
[5 empty] | 347.76 |  | 260.77
6 | Sub-Station Structures | 15.39 | LS | 1 | 15.39 | 0 | 0
| Sub-Total-A |  |  |  | 363.15 |  | 260.77
7 | Equipment Structure including Bus Bar, earthing, hardware fitting etc. @ 10 % |  |  |  | 36.315 |  | 26.077 | Part of Transformer and Bay, therefore included
8 | Power & Control Cables , earthmat etc. @ 13 % |  |  |  | 47.2095 |  | 16.9501 | Power and Control Cables portion charged @ 6.5%
9 | Spares @ 3% of 1 to 5 above |  |  |  | 10.4328 |  | 7.8231
10 | CST 4%, Transportation @5% , Insurance @1% Total 10 %( on 1 to 6) |  |  |  | 36.315 |  | 26.077
| Sub-Total |  |  |  | 493.4223 |  | 337.6971
11 | Storage @ 3% |  |  |  | 14.8027 |  | 10.1309
| Sub-Total |  |  |  | 508.225 |  | 347.8281
12 | Erection Charges @ 10 % |  |  |  | 50.8225 |  | 34.7828
| Sub-Total |  |  |  | 559.0475 |  | 382.6109
13 | Civil Works
| i) 132 kV Bay | 39.16 | No | 1 | 39.16 | 1 | 1
| ii) 11 kV bay | 18.57 | No | 1 | 18.57 | 1 | 1
| iii) Sub-Station Building | 56.17 | No | 1 | 56.17 | 0 | 0
| iv) Workshop Building | 8.43 | No | 1 | 8.43 | 0 | 0
| v) Workshop Machinery | 2.83 | No | 1 | 2.83 | 0 | 0
| Sub-Total |  |  |  | 684.2075 |  | 384.6109
14 | Contingency @ 3% |  |  |  | 20.5262 |  | 11.5383
| Sub-Total |  |  |  | 704.7337 |  | 396.1492
15 | Departmental charges @11 % |  |  |  | 77.5207 |  | 43.5764
| Sub-Total |  |  |  | 782.2544 |  | 439.7256
16 | Add. 12.36 % Service Tax on DC |  |  |  | 9.5816 |  | 5.386
| GRAND TOTAL |  |  |  | 791.836 |  | 445.1117
Calculation of Cost of 220/33 kV, 25/31.5 MVA Sub-Station | [6 empty] | Page-15
Sr. No. | Item Description | Rate (Rs Lac) | Unit | Qty | Amount (Rs Lac) | Quantity/Amount to be taken for normative rates as per Regulations 5(2)(i) |  | Remarks
[6 empty] | Qty. | Amount (Rs.Lac)
1 | 220/33 kV, 1x 25/31.5 MVA Transformer | 290.87 | No | 1 | 290.87 | 1 | 290.87
2 | 220 kV Equipment Transformer Bay
| Circuit Breaker | 24.09 | No | 1 | 24.09 | 1 | 24.09
| Control & Relay Panels | 6.47 | No | 2 | 12.94 | 2 | 12.94
| Isolators without Earth blade | 6.36 | No | 3 | 19.08 | 3 | 19.08
| Multicore Multi ratio CTs | 2.47 | No | 3 | 7.41 | 3 | 7.41
| Lighting Arrestors | 0.55 | No | 3 | 1.65 | 3 | 1.65
| PTs | 2.54 | No | 3 | 7.62 | 3 | 7.62
3 | 33 kV Equipments
| Circuit Breaker | 3.11 | No | 1 | 3.11 | 1 | 3.11
| Control & Relay Panels | 5.2 | No | 1 | 5.2 | 1 | 5.2
| Isolators without Earth blade | 0.55 | No | 2 | 1.1 | 2 | 1.1
| Multicore Multi ratio CTs | 0.28 | No | 3 | 0.84 | 3 | 0.84
| Lighting Arrestors | 0.05 | No | 3 | 0.15 | 3 | 0.15
| PTs | 0.18 | No | 3 | 0.54 | 3 | 0.54
4 | General Equipments
| DC Battery ( 400 AH) | 6.4 | No | 1 | 6.4 | 0 | 0
| Battery Charger | 2.14 | No | 2 | 4.28 | 0 | 0
| DCDB | 0.65 | No | 1 | 0.65 | 0 | 0
| Station T/F | 4.56 | No | 1 | 4.56 | 0 | 0
| ACDB | 4.91 | No | 1 | 4.91 | 0 | 0
5 | SCADA
| RTU | 23.33 | No | 1 | 23.33 | 0 | 0
| LDMS | 10.54 | No | 1 | 10.54 | 0 | 0
| FOTE | 18.23 | No | 2 | 36.46 | 0 | 0
[5 empty] | 465.73 |  | 374.6
6 | Sub-Station Structures | 43.96 | LS | 1 | 43.96 | 0 | 0
| Sub-Total-A |  |  |  | 509.69 |  | 374.6
7 | Equipment Structure including Bus Bar, earthing, hardware fitting etc. @ 10 % |  |  |  | 50.969 |  | 37.46 | Part of Transformer and Bay, therefore included
8 | Power & Control Cables , earthmat etc. @ 13 % |  |  |  | 66.2597 |  | 24.349 | Power and Control Cables portion charged @ 6.5%
9 | Spares @ 3% of 1 to 5 above |  |  |  | 13.9719 |  | 11.238
10 | CST 4%, Transportation @5% , Insurance @1% Total 10 %( on 1 to 6) |  |  |  | 50.969 |  | 37.46
| Sub-Total |  |  |  | 691.8596 |  | 485.107
11 | Storage @ 3% |  |  |  | 20.7558 |  | 14.5532
| Sub-Total |  |  |  | 712.6154 |  | 499.6602
12 | Erection Charges @ 10 % |  |  |  | 71.2615 |  | 49.966
| Sub-Total |  |  |  | 783.8769 |  | 549.6262
13 | Civil Works
| i) 220 kV Bay | 60.99 | No | 1 | 60.99 | 1 | 60.99
| ii) 33 kV bay | 18.57 | No | 1 | 18.57 | 1 | 18.57
| iii) Sub-Station Building | 70.22 | No | 1 | 70.22 | 0 | 0
| iv) Workshop Building | 8.43 | No | 1 | 8.43 | 0 | 0
| v) Workshop Machinery | 2.83 | No | 1 | 2.83 | 0 | 0
| Sub-Total |  |  |  | 944.9169 |  | 629.1862
14 | Contingency @ 3% |  |  |  | 28.3475 |  | 18.8756
| Sub-Total |  |  |  | 973.2644 |  | 648.0618
15 | Departmental charges @11 % |  |  |  | 107.0591 |  | 71.2868
| Sub-Total |  |  |  | 1080.3235 |  | 719.3486
16 | Add. 12.36 % Service Tax on DC |  |  |  | 13.2325 |  | 8.811
| GRAND TOTAL |  |  |  | 1093.556 |  | 728.1597
Calculation of Cost of 220/66 kV, 80/100 MVA Sub-Station | [6 empty] | Page-16
Sr. No. | Item Description | Rate (Rs Lac) | Unit | Qty | Amount (Rs Lac) | Quantity/Amount to be taken for normative rates as per Regulations 5(2)(i) |  | Remarks
[6 empty] | Qty. | Amount (Rs.Lac)
1 | 220/66 kV, 1x 80/100 MVA Transformer | 566.34 | No | 1 | 566.34 | 1 | 566.34
2 | 220 kV Equipment Transformer Bay
| Circuit Breaker | 24.09 | No | 1 | 24.09 | 1 | 24.09
| Control & Relay Panels | 6.47 | No | 2 | 12.94 | 2 | 12.94
| Isolators without Earth blade | 6.36 | No | 3 | 19.08 | 3 | 19.08
| Multicore Multi ratio CTs | 2.47 | No | 3 | 7.41 | 3 | 7.41
| Lighting Arrestors | 0.55 | No | 3 | 1.65 | 3 | 1.65
| PTs | 2.54 | No | 3 | 7.62 | 3 | 7.62
3 | 66 kV Equipments
| Circuit Breaker | 6.18 | No | 1 | 6.18 | 1 | 6.18
| Control & Relay Panels | 4.46 | No | 1 | 4.46 | 1 | 4.46
| Isolators without Earth blade | 2.12 | No | 2 | 4.24 | 2 | 4.24
| Multicore Multi ratio CTs | 0.72 | No | 3 | 2.16 | 3 | 2.16
| Lighting Arrestors | 0.19 | No | 3 | 0.57 | 3 | 0.57
| PTs | 0.8 | No | 3 | 2.4 | 3 | 2.4
4 | General Equipments
| DC Battery ( 400 AH) | 6.4 | No | 1 | 6.4 | 0 | 0
| Battery Charger | 2.14 | No | 2 | 4.28 | 0 | 0
| DCDB | 0.65 | No | 1 | 0.65 | 0 | 0
| Station T/F | 4.56 | No | 1 | 4.56 | 0 | 0
| ACDB | 4.91 | No | 1 | 4.91 | 0 | 0
5 | SCADA
| RTU | 23.33 | No | 1 | 23.33 | 0 | 0
| LDMS | 10.54 | No | 1 | 10.54 | 0 | 0
| FOTE | 18.23 | No | 2 | 36.46 | 0 | 0
[5 empty] | 750.27 |  | 659.14
6 | Sub-Station Structures | 43.96 | LS | 1 | 43.96 | 0 | 0
| Sub-Total-A |  |  |  | 794.23 |  | 659.14
7 | Equipment Structure including Bus Bar, earthing, hardware fitting etc. @ 10 % |  |  |  | 79.423 |  | 65.914 | Part of Transformer and Bay, therefore included
8 | Power & Control Cables , earthmat etc. @ 13 % |  |  |  | 103.2499 |  | 42.8441 | Power and Control Cables portion charged @ 6.5%
9 | Spares @ 3% of 1 to 5 above |  |  |  | 22.5081 |  | 19.7742
10 | CST 4%, Transportation @5% , Insurance @1% Total 10 %( on 1 to 6) |  |  |  | 79.423 |  | 65.914
| Sub-Total |  |  |  | 1078.834 |  | 853.5863
11 | Storage @ 3% |  |  |  | 32.365 |  | 25.6076
| Sub-Total |  |  |  | 1111.199 |  | 879.1939
12 | Erection Charges @ 10 % |  |  |  | 111.1199 |  | 87.9194
| Sub-Total |  |  |  | 1222.3189 |  | 967.1133
13 | Civil Works
| i) 220 kV Bay | 60.99 | No | 1 | 60.99 | 1 | 1
| ii) 66 kV bay | 31.31 | No | 1 | 31.31 | 1 | 1
| iii) Sub-Station Building | 70.22 | No | 1 | 70.22 | 1 | 1
| iv) Workshop Building | 8.43 | No | 1 | 8.43 | 1 | 1
| v) Workshop Machinery | 2.83 | No | 1 | 2.83 | 1 | 1
| Sub-Total |  |  |  | 1396.0989 |  | 972.1133
14 | Contingency @ 3% |  |  |  | 41.883 |  | 29.1634
| Sub-Total |  |  |  | 1437.9819 |  | 1001.2767
15 | Departmental charges @11 % |  |  |  | 158.178 |  | 110.1404
| Sub-Total |  |  |  | 1596.1599 |  | 1111.4171
16 | Add. 12.36 % Service Tax on DC |  |  |  | 19.5508 |  | 13.6134
| GRAND TOTAL |  |  |  | 1615.7107 |  | 1125.0305
Calculation of Cost of 220/132 kV, 80/100 MVA Sub-Station | [6 empty] | Page-17
Sr. No. | Item Description | Rate (Rs Lac) | Unit | Qty | Amount (Rs Lac) | Quantity/Amount to be taken for normative rates as per Regulations 5(2)(i) |  | Remarks
[6 empty] | Qty. | Amount (Rs.Lac)
1 | 220/132 kV, 1x 80 MVA Transformer | 496.72 | No | 1 | 496.72 | 1 | 496.72
2 | 220 kV Equipment Transformer Bay
| Circuit Breaker | 24.09 | No | 1 | 24.09 | 1 | 24.09
| Control & Relay Panels | 6.47 | No | 2 | 12.94 | 2 | 12.94
| Isolators without Earth blade | 6.36 | No | 3 | 19.08 | 3 | 19.08
| Multicore Multi ratio CTs | 2.47 | No | 3 | 7.41 | 3 | 7.41
| Lighting Arrestors | 0.55 | No | 3 | 1.65 | 3 | 1.65
| PTs | 2.54 | No | 3 | 7.62 | 3 | 7.62
3 | 132 kV Equipments
| Circuit Breaker | 7.89 | No | 1 | 7.89 | 1 | 7.89
| Control & Relay Panels | 4.46 | No | 1 | 4.46 | 1 | 4.46
| Isolators without Earth blade | 3.58 | No | 2 | 7.16 | 2 | 7.16
| Multicore Multi ratio CTs | 0.99 | No | 3 | 2.97 | 3 | 2.97
| Lighting Arrestors | 0.34 | No | 3 | 1.02 | 3 | 1.02
| PTs | 0.99 | No | 3 | 2.97 | 3 | 2.97
4 | General Equipments
| DC Battery ( 400 AH) | 6.4 | No | 1 | 6.4 | 0 | 0
| Battery Charger | 2.14 | No | 2 | 4.28 | 0 | 0
| DCDB | 0.65 | No | 1 | 0.65 | 0 | 0
| Station T/F | 4.56 | No | 1 | 4.56 | 0 | 0
| ACDB | 4.91 | No | 1 | 4.91 | 0 | 0
5 | SCADA
| RTU | 23.33 | No | 1 | 23.33 | 0 | 0
| LDMS | 10.54 | No | 1 | 10.54 | 0 | 0
| FOTE | 18.23 | No | 2 | 36.46 | 0 | 0
[5 empty] | 687.11 |  | 595.98
6 | Sub-Station Structures | 43.96 | LS | 1 | 43.96 | 0 | 0
| Sub-Total-A |  |  |  | 731.07 | 0 | 595.98
7 | Equipment Structure including Bus Bar, earthing, hardware fitting etc. @ 10 % |  |  |  | 73.107 |  | 59.598 | Part of Transformer and Bay, therefore included
8 | Power & Control Cables , earthmat etc. @ 13 % |  |  |  | 95.0391 |  | 38.7387 | Power and Control Cables portion charged @ 6.5%
9 | Spares @ 3% of 1 to 5 above |  |  |  | 20.6133 |  | 17.8794
10 | CST 4%, Transportation @5% , Insurance @1% Total 10 %( on 1 to 6) |  |  |  | 73.107 |  | 59.598
| Sub-Total |  |  |  | 992.9364 |  | 771.7941
11 | Storage @ 3% |  |  |  | 29.7881 |  | 23.1538
| Sub-Total |  |  |  | 1022.7245 |  | 794.9479
12 | Erection Charges @ 10 % |  |  |  | 102.2724 |  | 79.4948
| Sub-Total |  |  |  | 1124.9969 |  | 874.4427
13 | Civil Works
| i) 220 kV Bay | 60.99 | No | 1 | 60.99 | 1 | 1
| ii) 132 kV bay | 39.16 | No | 1 | 39.16 | 1 | 1
| iii) Sub-Station Building | 70.22 | No | 1 | 70.22 | 0 | 0
| iv) Workshop Building | 8.43 | No | 1 | 8.43 | 0 | 0
| v) Workshop Machinery | 2.83 | No | 1 | 2.83 | 0 | 0
| Sub-Total |  |  |  | 1306.6269 |  | 876.4427
14 | Contingency @ 3% |  |  |  | 39.1988 |  | 26.2933
| Sub-Total |  |  |  | 1345.8257 |  | 902.736
15 | Departmental charges @11 % |  |  |  | 148.0408 |  | 99.301
| Sub-Total |  |  |  | 1493.8666 |  | 1002.037
16 | Add. 12.36 % Service Tax on DC |  |  |  | 18.2978 |  | 12.2736
| GRAND TOTAL |  |  |  | 1512.1644 |  | 1014.3106

## Page-10
Page 10
Calculations of cost of 33/11 kV, Sub-Stations and line based on approved cost data for the year 2011-12
S.No. | Description of item | Iss.No. REC STD No. | Unit | Qty | Rate | Amount | Quantity/Amount to be taken for normative rates as per Regulations 5(2)(i)
[7 empty] | Qty | Amount
A) | Sub-Station Transformer
| 100 kVA, 33/0.4 kV S/Stn, Transformer |  | No. | 1 | 283068 | 283068 | 0 | 0
B) | 33 kV Switchgear Equipment
1 | 33 kV Control and Relay Panel without Differential Relay |  | No. | 1 | 246482 | 246482 | 1 | 246482
2 | 33 kV CT's Single Unit | 2705/1992 | No. | 3 | 28464 | 85392 | 3 | 85392
3 | 33/11 kV, single phase PT's | 3156/1992 | No. | 3 | 21462 | 64386 | 3 | 64386
4 | 400A 33 kV Isolator with E/Blade | 9921/1992 | No. | 1 | 78778 | 78778 | 1 | 78778
5 | 400A 33 kV Isolator without E/Blade | 9921/1992 | No. | 4 | 72326 | 289304 | 4 | 289304
6 | 33 kV lightening arresters metal oxide type | 55/1987 | set | 3 | 13940 | 41820 | 3 | 41820
7 | 33 kV Expulsion Dropout fuse unit | 5292/1970 | set | 1 | 8989 | 8989 | 1 | 8989
| S/Total (B) :- |  |  |  |  | 815151 |  | 815151
C) | 11 kV switchgear and allied Equipment
(I) | 11 kV panel board with 1 incomer panel with PT's |  | set | 1 | 2318520 | 2318520 | 1 | 2318520
for one outgoing feeder
(II) | 11 kV triple pole GO Switch/Isolator without E/blade for S/Stn with |  | No. | 1 | 4491 | 4491 | 1 | 4491
| one outgoing feeder | 1326/1977
(III) | 11 kV LA's Sub-Station Type for S/Stn with |  | No. | 3 | 358 | 1074 | 3 | 1074
1 outgoing Feeder
(IV) | 95 mm2, 11kV grade cable for S/Stn with |  | mtr. | 50 | 706 | 35300 | 50 | 35300
1 no. of out going Feeder
(V) | 11 kV epoxy terminating kits for S/Stn with
| 1 no. of out going Feeder |  | No. | 1 | 7412 | 7412 | 1 | 7412
(VI) | HT compound & other material in sets for cable boxes
| of panels,S/Stn with 1 no. of out going Feeder |  | No. | 4 | 2038 | 8152 | 4 | 8152
| S/Total (C) :- |  |  |  |  | 2374949 |  | 2374949
D) | General Equipment
1 | 30 V, 100 AH-Ni-Cd battery alongwith Battery charger | 34/1981 | No. | 1 | 106396 | 106396 | 0 | 0
2 | 400 V, A.C. distribution switchgear | 4047/1967 | No. | 1 | 481197 | 481197 | 0 | 0
| S/Total (D) :- |  |  |  |  | 587593 |  | 0
E) | Super structure & busbar
I | 33 kV super structure & busbar as per Page -33 of Cost Data |  | job | 1 | 562030 | 562030 | 1 | 562030
II | 11 kV super structure & busbar detail as per for Sub-Station
| with 1 no. of out going Feeder as per page -36 of cost data |  | job | 1 | 155580 | 155580 | 1 | 155580
| S/Total (E) :- |  |  |  |  | 717610 |  | 717610
F | Earthing of 33 kV Sub-Station Equipments as per P-38 of cost data |  | job | 1 | 223410 | 223410 | 1 | 223410
G | Yard & colony fencing as per detail (P-43)(Cost data) |  | job | 1 | 379780 | 379780 | 0 | 0
H | Yard lightening as per detail (P-44)(Cost Data) |  | job | 1 | 108770 | 108770 | 0 | 0
I | Control and LT power cables as per detail (P-45)(Cost Data) |  | job | 1 | 70510 | 70510 | 1 | 70510
J) | Foundation of :--
1 | Transformer as per detail (P-46)(Cost data) |  | job | 1 | 36690 | 36690 | 1 | 36690
K | Cost of trenches as per detail (P-50)(Cost data) |  | job | 1 | 275930 | 275930 | 0 | 0
| S/Total (F to K) :- |  |  |  |  | 1095090 |  | 330610
| Grand Total (A to K ) :- |  |  |  |  | 5873461 |  | 4238320
Cost of 1x3.15 MVA, Terminal Equipment & Sub-Station (Manned) with one 11 kV Outgoing feeder
S.No. | Description of item | Iss.No. | Unit | Qty | Rate | Amount
|  | REC STD |  |  |  | 4 Nos.
No.
1 | Cost of 1x3.15MVA,33/11 kV Terminal Sub-Station With 1 outgoing feeder |  | No. | 1 | -- | 5873461 | 1 | 4238320
2 | 3.15 MVA, 33/11 kV Transformer | 2026/1993 | No. | 1 | 2732591 | 2732591 | 1 | 2732591
3 | 185 mm2. 11 kV grade cable | 7098/1985 | No. | 50 | 978 | 48900 | 50 | 48900
|  | S/Total :- |  |  |  | 8654952 |  | 7019811
| Add :- storage @ 3.0 %, contingencies @ 3%& |  |  |  |  | 1471341.84 |  | 1193367.87
Departmental charges @ 11 % = Total @ 17%
| Transportation charges as per statement (P-61 of Cost Data) |  |  |  |  | 294290 |  | 294290
| Erection charges as per statement(P-75 of Cost Data ) |  |  |  |  | 3272726 |  | 3272726
| Cost of control room building as per detail(P-51 Cost Data ) |  |  |  |  | 2553922 |  | 0
| Service Tax |  |  |  |  | 117672.7274 |  | 95441.3504
|  | Total :- |  |  |  | 16364904.5674 |  | 11875636.2204
| 33 kV line (100mm2 AAAC ) | (PCC: ST 60:40) |  |  |  |  | 801834
|  | (Page 2 of Cost data) |  |  | Service Tax on DC= |  | 6490.4993
|  |  | Cost per kM |  |  |  | 808324.4993

## Page-21
Page-21
Calculations of ratings of 66 kV 132 kV or 220 kV conductors:
Sr. No. | Conductor | Current Carrying Capacity as per IS:398 Part-IV-1994, & IS 398 at 75degree C Temp. | Voltage | MVA capacity keeping 30% redundancy
1 | Wolf | 395 | 66 | 31.6073
2 | Panther | 475 | 132 | 76.0175
3 | Zebra | 735 | 220 | 196.0451
4 | ACSR 50mm2 | 195 | 11 | 2.6006
5 | ACSR 50mm2 | 195 | 0.4 | 0.094567
6 | AAAC Dog (100mm2) | 325 | 33 | 13.003

## Annexure-A(page-3)
|  | Page-3 |  | Annexure-A
Abstract of proposal for normative charges as per approved cost data for the year 2011-12.
Sr. No. | Range of Connected Load | Category of Consumers | Expenses for the distribution system other than service lines (as per Regulation 5(2) | Expenses for providing Service line | Remarks
per kVA normative charges ( `)
1 | 2 | 3 | 4 | 8
A) | Connected load up to 20 kW [ Supply Voltage LT 1-Phase/3-Phase] | Domestic Supply per kW on connected load( Single Part Tariff) | 910 | Line rates as per approved cost data for the year 2011-12 | Rates per kW (in case of single part and per kVA in case of two part tariff for 22 kV consumers shall be calculated by multiplying the rates at 11 kV with 1.20 multiplication factor ( as calculated )
|  | Non-residential Supply per kW on connected load (single part tariff) | 1220 | Line rates as per approved cost data for the year 2011-12
B) | Connected load >20 kW and up to 50 kW [Supply Voltage 3phase LT] | All category of Consumers per kVA on contract demand | 2740 | Line rates as per approved cost data for the year 2011-12
C) | Connected load between 51 kW and 1000 kW for furnace/rolling mills and up to 2000 kW for general load[ 11 kV supply Voltage] | All category of Consumers per kVA on contract demand | 4870 | Line rates as per approved cost data for the year 2011-12
D) | Connected load between 1000 kW and 10000 kW for PIU and between 2000 and 10000 kW for general load [ Supply Voltage 33 kV ] | All category of Consumers per kVA on contract demand | 4640 | Line rates as per approved cost data for the year 2011-12
E) | Connected load between 1000 kW and 10000 kW for PIU and between 2000 and 10000 kW for general load [ Supply Voltage 66 kV ]
|  | All category of Consumers per kVA on contract demand | 4260 | Line rates as per approved cost data for the year 2011-12
F) | Connected load between 10000 kW and above and load to be released at 132 kV or 220 kV | All category of Consumers per kVA on contract demand | 4090 | Line rates as per approved cost data for the year 2011-12
Sd/-
Petitioner

## page -7
Page No-7
Lengths of HT/EHT/LT lines taken for calcualtion of normative rates based on CAPEX Plan
220 kV
Sr. No. | Line detail | Length (kM)
1 | 220 kV line from PGCIL Sub/Stn Reeru Majra to Nalagarh and then to Baddi | 7.2
2 | 220 kV line from Jamta to Kala Amb | 36.716
3 | 220 kV line from Nalagarh to Baddi | 25
4 | 220 KV line from Rauri to Kunihar | 24
5 | 220 kV line from Kangoo to Mattansidh | 42
| Average length | 26.9832
| Length of 220 kV, line taken | 27 | kM
132 kV
Sr. No. | Line detail | Length (kM)
1 | 132 kV line from LILO of Kunihar -Jutog line to Maliana | 33.96
2 | 132 kV line from LILO Mattansidh-Kangoo line to Jahoo | 10.62
3 | 132 kV line from Una to Tahliwala | 32.62
| Average length | 25.7333
| Length of 220 kV, line taken | 26 | kM
66 kV
Sr. No. | Line detail |  |  | Length (kM)
1 | 66 kV line from Baddi to Nalagarh |  |  | 49.35
| In view of single line in the capax plan, and the lengths of 132 kV and 220 kV lines, the length taken is half the single length |  |  | 25
33 kV & 11 kV lines for 33/11 kV Sub-Stations
Sr. No. | Feeder detail | 33 kV line Length (kM) | 22 or 11 kV line length
1 | 33/11 kV, Dharampur | 4 | 12
2 | 33/11 kV, Dhabota | 4 | 10
3 | 33/11 kV, Goela | 18 | 15.5
4 | 33/11 kV, Chail | 25 | 14
5 | 33/11 kV, Basal | 4 | 7
6 | 33/11 kV, Narainy | 20 | 20
7 | 33/11 kV, Kupvi | 27 | 22
8 | 33/11 kV, Sub-Station at Bharoli | 10 | 7
9 | 33/11 kV, Sub-Station at Holta | 10 | 10
10 | 33/11 kV Sub-Station at Chak Sarai | 14 | 11
11 | 33/11 kV, Sub-Station at Santokhgarh | 8.5 | 14
12 | 33/11 kV, Sub-Station at Attara | 8 | 9
13 | 33/22 kV, Karsog | 4 | 0
14 | 33/11 kV, Jai Devi | 0.7 | 0
15 | 33 kV line from Jaisinghpur to Chadiar Sub-Station | 5
16 | 33 kV line between Khauli HEP to 33/11 kV, Gaj | 7
17 | 33 kV line from Gohar to Pandoh | 20
18 | 33 kV line from Makreri to Lad Bharol | 21.8
19 | 33 kV line from Jahu to Barchwar | 12.12
20 | 33 kV line from Kotla to Talai(Jhabola) | 15
21 | 33 kV line from Jahu to Kakkar | 13
22 | 33 kV line from Tauni Devi to Bhoranj | 9.535
| Total | 260.655 | 151.5
| Average length | 11.848 | 10.8214
| Say(kM) | 12 | 11
Transformer Ratings taken in the calculations
1) | 132/33 kV & 132/11 KV Sub-Stations | 25/31.5 MVA
As per Capex Plan for the FY 12-13 under control period FY 12-14, the ratings of new or augmentation of sub-stations are 25/31.5 MVA and where the ratings are 16 MVA , the same have been proposed to augmented to 25/31.5 MVA. Therefore, the rating has been taken as 25/31.5 MVA
2) | 220/66 kV, Sub-Stations = | 80/100 MVA
The ratings of 220/66 kV Sub-Station proposed under CAPEX Plan is 80/100 MVA . The rating of 220/66 kV, Sub-Station is ,therefore taken as 80/100 MVA
3) | 220/33 kV, Sub-Station | 25/31.5 MVA
4) | 66/33 kV, & 66/11 kV | 20 MVA
5) | 220/132 kV | 80/100 MVA
6) | 33/11 kV | 3.15 MVA
7) | DRS
Average of 25 kVA, 63 kVA and 100 kVA
| New Sub-Stations as per CAPEX | 1636
| New 11 kV lV lines | 1255.76 | No
| New LT line | 1800.18 | kM
| 11 kV line per DTR | 0.76758 | kM
| LT lines per DTR | 1.1004 | kM
The 11 kV and LT lines I the capex plan inclding the lines for express feeders and new LT feeders from the existing DTRs. Keeping this fact in view, the follong line lenghts have been poposed for normative rates:-
HT line per DTR = 0.25 kM
LT lines DTR = 0.125 kM

## Page No 8-9
Page No. 8 & 9
Calcualtions of cost of DTRS, 11 kV & LT lines based on approved cost data for the year 2011-12
Sr. No. | DESCRIPTION | REC SPEC 3 | ISS.NO. | QTY | UNIT | RATE | Rates as per cost data |  |  |  | Normative Charges as per Regulation 5(2)(i)
[7 empty] | 25 KVA | 63 KVA | 100 KVA | 250 KVA | 25 KVA | 63 KVA | 100 KVA | 250 KVA
1 | 11/0.4kV DISTRIBUTION TRANSFORMER | (ORD)11/1976
| I)25kVA |  |  | 1 | No | 48751 | 48751 |  |  |  | 48751
| II)63kVA |  |  | 1 | No | 87750 |  | 87750 |  |  |  | 87750
| III)100kVA |  |  | 1 | No | 121876 |  |  | 121876 |  |  |  | 121876
| IV) 250 KVA |  |  | 1 | No | 198503 |  |  |  | 198503 |  |  |  | 198503
2 | S/T POLE 9MTR.W/L200KG |  | 2713/1980 | 2 | No | 7584 | 15168 | 15168 | 15168 | 15168 | 15168 | 15168 | 15168 | 15168
3 | MUFF |  |  | 2 | No | 980 | 1960 | 1960 | 1960 | 1960 | 1960 | 1960 | 1960 | 1960
4 | CI (2800X100X50)MM FOR X-ARM | F-3/1981 |  | 4 | No | 1367 | 5468 | 5468 | 5468 | 5468 | 5468 | 5468 | 5468 | 5468
TRANSFORMER BASE MAIN CHANNEL
5 | C.I (460X100X50)MM FOR SUPPORTING | DO |  | 2 | No | 225 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450
MAIN CHANNEL OF TRANSFORMER
6 | TRANSFORMER BELTING
| I)ANGLE FOR (2800X50X50)MM | DO |  | 2 | No | 642 | 1284 | 1284 | 1284 | - | 1284 | 1284 | 1284 | -
| II)-DO- (460X35X35)MM |  |  | 2 | No | 94 | 188 | 188 | 188 | - | 188 | 188 | 188 | -
7 | TRANSFORMER BED ( 1.2X1.5X1.5) M |  |  | 1 | L/S | - | - | - | - | 20000 | - | - | - | 20000
8 | CI (2800X75X40)MMFOR FUSE UNIT AB SWITCH |  |  | 4 | No | 1019 | 4076 | 4076 | 4076 | 4076 | 4076 | 4076 | 4076 | 4076
9 | A.I X ARM (2800X50X50)MM FOR | DO |  | 1 | No | 642 | 642 | 642 | 642 | 642 | 642 | 642 | 642 | 642
LIGHTING ARRESTOR
10 | G.O.SWITCH 400A | 43/1987 | 9921.P-I-IV | 1 | Set. | 4491 | 4491 | 4491 | 4491 | 4491 | 4491 | 4491 | 4491 | 4491
11 | D.O.FUSE | 53/1987 | 9385 | 1 | Set. | 1497 | 1497 | 1497 | 1497 | 1497 | 1497 | 1497 | 1497 | 1497
PART-I & II
12 | LIGHTING ARRESTOR | 10/1976 | 3070/1974 | 3 | No | 358 | 1074 | 1074 | 1074 | 1074 | 1074 | 1074 | 1074 | 1074
13 | DISC INSULATOR WITH FITTING | 3/1971 | 73/1971 | 3 | Set. | 954 | 2862 | 2862 | 2862 | 2862 | 2862 | 2862 | 2862 | 2862
14 | STAY SET COMPLETE | 25/85 | 2141/1969 | 2 | Set. | 776 | 1552 | 1552 | 1552 | 1552 | 0 | 0 | 0 | 0
15 | STAY WIRE 7/3.15 mm ( @ 6.0 kg Per Stay Set) |  |  | 12 | Kg. | 57 | 684 | 684 | 684 | 684 | 0 | 0 | 0 | 0
16 | PIPE EARTHING |  |  | 3 | Set. | 2336 | 7008 | 7008 | 7008 | 7008 | 0 | 0 | 0 | 0
17 | LT DISTRIBUTION PANEL BOX WITH MCCB | 2516 (Part-I&II) |  | 1 | Set. | 6975 | 6975 | 6975 | 6975 | 6975 | 0 | 0 | 0 | 0
18 | HALF CLAMPS |  |  | 15 | No. | 61 | 915 | 915 | 915 | 915 | 915 | 915 | 915 | 915
19 | M.S. NUTS &BOLTS OFF SIZES |  |  | 10 | Kg. | 82 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820
20 | G.I.THIMBLE |  |  | 16 | No | 28 | 448 | 448 | 448 | 448 | 448 | 448 | 448 | 448
21 | LEAD TIN SOLDER 60:40 |  |  | 0.75 | Kg. | 749 | 561.75 | 561.75 | 561.75 | 561.75 | 0 | 0 | 0 | 0
22 | SOLDER FLUX |  |  | 1 | Tin | 90 | 90 | 90 | 90 | 90 | 0 | 0 | 0 | 0
23 | DANGER PLATE | F-3/81 |  | 1 | No | 101 | 101 | 101 | 101 | 101 | 0 | 0 | 0 | 0
24 | BARBED WIRE | DO |  | 15 | Kg. | 59 | 885 | 885 | 885 | 885 | 885 | 885 | 885 | 885
24 | L.T. CABLE 3.5 CORE | D0 | 1554 PART-I 1976
| i) 25MM2 |  |  | 10 | Mtr | 54 | 540 |  |  |  | 540
| ii) 50MM2 |  |  | 10 | Mtr | 96 |  | 960 |  |  |  | 960
| iii )95MM2 |  |  | 10 | Mtr | 170 |  |  | 1700 |  |  |  | 1700
| iv) 185 MM2 |  |  | 10 | Mtr | 328 |  |  |  | 3280 |  |  |  | 3280
25 | ENERGY METER 3-P, 4-WIRE |  | 722 P-1&III
| i) 50 A CT TYPE |  |  | 1 | No | 8078 | 8078 |  |  |  | 0
| ii) 100 A CT TYPE | 250.44 |  | 1 | No | 8078 |  | 8078 |  |  |  | 0
| iii) 200 A CT TYPE |  |  | 1 | No | 8078 |  |  | 8078 |  |  |  | 0
| iv) 400 A CT TYPE |  |  | 1 | No | 7781 |  |  |  | 7781 |  |  |  | 0
26 | ALUMINUM PAINT. |  |  | 4 | Ltr | 117 | 468 | 468 | 468 |  | 468 | 468 | 468
[5 empty] | SUB-TOTAL: - |  | 117036.75 | 156455.75 | 191321.75 | 287291.75 | 91987 | 131406 | 166272 | 262539 | 25049.75
27 | ERECTION CHARGES AS PER S-HEAD -C ( as per Cost Data Page 50 excluding item No. i, j & l)) | [5 empty] | 42492 | 42492 | 42492 | 42492 | 37001 | 37001 | 37001 | 37001
28 | TRANSPORTATION CHARGES AS PER | [5 empty] | 14268 | 15070 | 16273 | 17476 | 14268 | 15070 | 16273 | 17476
STATEMENT-VI.(59)
29 | OTHER CHARGES
| I) CONTIGENCY@3% | [5 empty] | 3511.1025 | 4693.6725 | 5739.6525 | 8618.7525 | 2759.61 | 3942.18 | 4988.16 | 7876.17
| ii) STORAGE @3% | [5 empty] | 3511.1025 | 4693.6725 | 5739.6525 | 8618.7525 | 2759.61 | 3942.18 | 4988.16 | 7876.17
| iii) DEPTT. CHARGES @11% | [5 empty] | 12874 | 17210 | 21045 | 31602 | 10118.57 | 14454.66 | 18289.92 | 28879.29
| iv) Service Tax on DC @ 12.36% | [5 empty] | 1591.2264 | 2127.156 | 2601.162 | 3906.0072 | 1250.6553 | 1786.596 | 2260.6341 | 3569.4802
[5 empty] | G. TOTAL |  | 195284.1814 | 242742.251 | 285212.217 | 400005.2622 | 160144.4453 | 207602.616 | 250072.8741 | 365217.1102
1) | 11 kV line (50 mm2 ACSR conductor) |  |  |  | (PCC:ST 60:40) |  | 335600
[6 empty] | DC | 22239.4
[6 empty] | ST | 2748.7898
338348.7898
2) | LT lines (50mm2 ACSR Conductor) |  |  |  | (PCC:ST 60:40) |  | 319480
[6 empty] | DC | 21492.2
[6 empty] | ST | 2656.4359
322136.4359
Working out the factor for cost of 22 kV works
| Distribution Sub-Stations Cost | 25 KVA | 63 KVA | 100 KVA | 250 KVA
| 11/.4 kV | 195284.1814 | 242742.251 | 285212.217 | 400005.2622
| 22/.4 kV | 250727.89 | 315462.4448 | 388892.4188 | 550939.6208
| ratio | 1.2839 | 1.2996 | 1.3635 | 1.3773
Line Costs per kM
| 11 kV | 304517.6236
| 22 kV | 335473.2208
| ratio | 1.1017
| Average ratio | 1.2
For 22 kV works the charges are proposed by taking above factor of 1.20 on the rates for 11 kV consumers.